## NPE7-EAI-41XX-XXX-RG-XA-007522_
[57 empty] | Internal Doc. Nº: |  | 225-001-L-I-07522
|  |  |  | CMS BOP I/O HARDWIRED SIGNAL LIST | [52 empty] | NLWA Doc. Nº: |  | NPE7-EAI-41XX-XXX-RG-XA-007522
[57 empty] | Contractor Doc Nº: |  | NLHP-41XX-IE-LT-EAI-7522
| Project: | NORTH LONDON
OWNER | POINTNAME | FLD_DEV | 3_KKS | DESC | LONG DESC | ACTIVE | INACTIVE | EST | PRI | SIG_TYPE | SIG_LEVEL | PWR_SRC | NOMINAL POWER | LINE MONITORING | LOCATION | DEV_PARTITION | DEVICE_LO | DEVICE_HI | DEVICE_UNITS | DISPLAY_LO | DISPLAY_HI | DISPLAY_UNITS | PRECISION_SIGNAL | SOE | HIST | PID | LOGIC | SCHEM | HMI_SCREEN | Intelligent System | Signal Loss | Instrument Function | KKS_Junction Box | Explosion Protection | IS | IS_MODEL | IS_IN_TB_1 | IS_IN_TB_2 | IS_OUT_TB_1 | IS_OUT_TB_2 | CONTROLLER | CABINET_KKS | CARD_ID | CARD_TYPE | CARD_POINT_Nº | TA_MODEL | TA_TAG_ID | MC_ID | MC_TERM_STRIP_ID | TB_1 | TB_2 | TB_3 | TB_4 | STATUS OF TECHNICAL DATA | IN PAMELA | REMARKS | MOD | REV | REV_COMMENT | REV_DATE
EA-I&C | A0GHB10AA301XB01 | A0GHB10AA301 | XB01 | Svce Wtr Tnk Mkup Vlv | Service Water Tank Makeup Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB10AA301XB02 | A0GHB10AA301 | XB02 | Svce Wtr Tnk Mkup Vlv | Service Water Tank Makeup Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB10AA301YB02 | A0GHB10AA301 | YB02 | Svce Wtr Tnk Mkup Vlv | Service Water Tank Makeup Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB10CL001AXQ01 | A0GHB10CL001A | XQ01 | Service Water Tank Lvl 1 | Service Water Tank Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB10CL001BXQ01 | A0GHB10CL001B | XQ01 | Service Water Tank Lvl 2 | Service Water Tank Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB20CP001XQ01 | A0GHB20CP001 | XQ01 | Svce Wtr Press Grp Inl Fltr DP | Service Water Pressure Group Inlet Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Pressure Group Supplier | A0GHB30BU001XB01 | A0GHB30BU001 | XB01 | Svce Wtr Press Grp | Service Water Pressure Group | Pump1 Running |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Pressure Group Supplier | A0GHB30BU001XB02 | A0GHB30BU001 | XB02 | Svce Wtr Press Grp | Service Water Pressure Group | Pump2 Running |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Pressure Group Supplier | A0GHB30BU001XB03 | A0GHB30BU001 | XB03 | Svce Wtr Press Grp | Service Water Pressure Group | Pump3 Running |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Pressure Group Supplier | A0GHB30BU001XB33 | A0GHB30BU001 | XB33 | Svce Wtr Press Grp | Service Water Pressure Group | n Anomaly | Anomaly |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Pressure Group Supplier | A0GHB30BU001YB45 | A0GHB30BU001 | YB45 | Svce Wtr Press Grp | Service Water Pressure Group | Start Permissive |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB40CP001XQ01 | A0GHB40CP001 | XQ01 | Svce Wtr Press Grp Outl Press | Service Water Pressure Group Outlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | A0GHB41CQ001XQ01 | A0GHB41CQ001 | XQ01 | Svce Wtr Tnk Inl NaClO | Service Water Tank Inlet Sodium Hypochlorite | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB44AA301XB01 | A0GHB44AA301 | XB01 | B1: Svce Wtr to Proc Wtr Tnk Blr IV | B1: Service Water to Process Water Tank Boiler Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB44AA301XB02 | A0GHB44AA301 | XB02 | B1: Svce Wtr to Proc Wtr Tnk Blr IV | B1: Service Water to Process Water Tank Boiler Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB44AA301YB02 | A0GHB44AA301 | YB02 | B1: Svce Wtr to Proc Wtr Tnk Blr IV | B1: Service Water to Process Water Tank Boiler Isolation Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB44AA302XB01 | A0GHB44AA302 | XB01 | B2: Svce Wtr to Proc Wtr Tnk Blr IV | B2: Service Water to Process Water Tank Boiler Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB44AA302XB02 | A0GHB44AA302 | XB02 | B2: Svce Wtr to Proc Wtr Tnk Blr IV | B2: Service Water to Process Water Tank Boiler Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB44AA302YB02 | A0GHB44AA302 | YB02 | B2: Svce Wtr to Proc Wtr Tnk Blr IV | B2: Service Water to Process Water Tank Boiler Isolation Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB55AA301XB01 | A0GHB55AA301 | XB01 | Svce Wtr to Blr WstWtr Pit Vlv | Service Water to Boiler Waste Water Pit Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB55AA301XB02 | A0GHB55AA301 | XB02 | Svce Wtr to Blr WstWtr Pit Vlv | Service Water to Boiler Waste Water Pit Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB55AA301YB02 | A0GHB55AA301 | YB02 | Svce Wtr to Blr WstWtr Pit Vlv | Service Water to Boiler Waste Water Pit Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB81CP001XQ01 | A0GHB81CP001 | XQ01 | Emerg BlwDn Attemp Pmp1 Suct Fltr DP | Emergency Blowdown Attemperation Pump 1 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB82CP001XQ01 | A0GHB82CP001 | XQ01 | Emerg BlwDn Attemp Pmp2 Suct Fltr DP | Emergency Blowdown Attemperation Pump 2 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB90CF001XQ01 | A0GHB90CF001 | XQ01 | Emerg BlwDn Attemp Pmps Disch Flow | Emergency Blowdown Attemperation Pumps Discharge Flow | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB90CP001XQ01 | A0GHB90CP001 | XQ01 | Emerg BlwDn Attemp Pmps Disch Press | Emergency Blowdown Attemperation Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB93AA401XQ13 | A0GHB93AA401 | XQ13 | B1: Emerg BlwDn Attemp CV | Boiler 1: Emergency Blowdown Attemperation Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB93AA401YQ01 | A0GHB93AA401 | YQ01 | B1: Emerg BlwDn Attemp CV | Boiler 1: Emergency Blowdown Attemperation Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB94AA401XQ13 | A0GHB94AA401 | XQ13 | B2: Emerg BlwDn Attemp CV | Boiler 2: Emergency Blowdown Attemperation Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB94AA401YQ01 | A0GHB94AA401 | YQ01 | B2: Emerg BlwDn Attemp CV | Boiler 2: Emergency Blowdown Attemperation Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB95AA401XQ13 | A0GHB95AA401 | XQ13 | B1: Atm Blr BlwDn Tnk Lvl CV | Boiler 1: Atmospheric Boiler Blowdown Tank Level Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB95AA401YQ01 | A0GHB95AA401 | YQ01 | B1: Atm Blr BlwDn Tnk Lvl CV | Boiler 1: Atmospheric Boiler Blowdown Tank Level Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB96AA401XQ13 | A0GHB96AA401 | XQ13 | B2: Atm Blr BlwDn Tnk Lvl CV | Boiler 2: Atmospheric Boiler Blowdown Tank Level Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | A0GHB96AA401YQ01 | A0GHB96AA401 | YQ01 | B2: Atm Blr BlwDn Tnk Lvl CV | Boiler 2: Atmospheric Boiler Blowdown Tank Level Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Clinical Waste Supplier | B0GA_10GH001XB31 | B0GA_10GH001 | XB31 | Clinical Waste Interface | Clinical Waste Interface | No General Alarm | General Alarm |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | - | NPE7-EAI-41XX-XXX-PP-XA-007645 | NPE7-EAI-41XX-XXX-PP-XA-007641 | NPE7-EAI-41XX-XXX-IM-XA-007645 | Clinical Waste Treatment System | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Clinical Waste Supplier | B0GA_10GH001XB33 | B0GA_10GH001 | XB33 | Clinical Waste Interface | Clinical Waste Interface | PLC n fail | PLC fail |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | - | NPE7-EAI-41XX-XXX-PP-XA-007645 | NPE7-EAI-41XX-XXX-PP-XA-007641 | NPE7-EAI-41XX-XXX-IM-XA-007645 | Clinical Waste Treatment System | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GAA10CL001AXQ01 | B0GAA10CL001A | XQ01 | Raw Wtr Pmps Pit Lvl 1 | Raw Water Pumps Pit Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | TBD | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000013 - Raw Water | NPE7-EAI-41XX-XXX-PP-XA-007618 | NPE7-EAI-41XX-XXX-PP-XA-007636 | NPE7-EAI-41XX-XXX-IM-XA-007614 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD | To be located in the existing pumping station far away from the ERF building | A | P01 |  | 2023-03-24
EA-I&C | B0GAA10CL001BXQ01 | B0GAA10CL001B | XQ01 | Raw Wtr Pmps Pit Lvl 2 | Raw Water Pumps Pit Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | TBD | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000013 - Raw Water | NPE7-EAI-41XX-XXX-PP-XA-007618 | NPE7-EAI-41XX-XXX-PP-XA-007636 | NPE7-EAI-41XX-XXX-IM-XA-007614 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD | To be located in the existing pumping station far away from the ERF building | A | P01 |  | 2023-03-24
RW Screening Supplier | B0GAA10GH001XB31 | B0GAA10GH001 | XB31 | Raw Water Screening Interface | Raw Water Screening Interface | No General Alarm | General Alarm |  |  | DI | 24VDC | S |  |  | TBD |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000013 - Raw Water | NPE7-EAI-41XX-XXX-PP-XA-007618 | NPE7-EAI-41XX-XXX-PP-XA-007636 | NPE7-EAI-41XX-XXX-IM-XA-007614 | Motorized Travelling EEL Screen Filter | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD | To be located in the existing pumping station far away from the ERF building | A | P01 |  | 2023-03-24
RW Screening Supplier | B0GAA10GH001XB33 | B0GAA10GH001 | XB33 | Raw Water Screening Interface | Raw Water Screening Interface | PLC n fail | PLC fail |  |  | DI | 24VDC | S |  |  | TBD |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000013 - Raw Water | NPE7-EAI-41XX-XXX-PP-XA-007618 | NPE7-EAI-41XX-XXX-PP-XA-007636 | NPE7-EAI-41XX-XXX-IM-XA-007614 | Motorized Travelling EEL Screen Filter | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD | To be located in the existing pumping station far away from the ERF building | A | P01 |  | 2023-03-24
RW Screening Supplier | B0GAA20AA301XB01 | B0GAA20AA301 | XB01 | Raw Wtr Pmps Fltr 1 Disch MOV | Raw Water Pumps Filter 1 Discharge Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | TBD |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000013 - Raw Water | NPE7-EAI-41XX-XXX-PP-XA-007618 | NPE7-EAI-41XX-XXX-PP-XA-007636 | NPE7-EAI-41XX-XXX-IM-XA-007614 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD | To be located in the existing pumping station far away from the ERF building | A | P01 |  | 2023-03-24
RW Screening Supplier | B0GAA20AA301XB02 | B0GAA20AA301 | XB02 | Raw Wtr Pmps Fltr 1 Disch MOV | Raw Water Pumps Filter 1 Discharge Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | TBD |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000013 - Raw Water | NPE7-EAI-41XX-XXX-PP-XA-007618 | NPE7-EAI-41XX-XXX-PP-XA-007636 | NPE7-EAI-41XX-XXX-IM-XA-007614 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD | To be located in the existing pumping station far away from the ERF building | A | P01 |  | 2023-03-24
RW Screening Supplier | B0GAA20AA301XB07 | B0GAA20AA301 | XB07 | Raw Wtr Pmps Fltr 1 Disch MOV | Raw Water Pumps Filter 1 Discharge Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | TBD |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000013 - Raw Water | NPE7-EAI-41XX-XXX-PP-XA-007618 | NPE7-EAI-41XX-XXX-PP-XA-007636 | NPE7-EAI-41XX-XXX-IM-XA-007614 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD | To be located in the existing pumping station far away from the ERF building | A | P01 |  | 2023-03-24
RW Screening Supplier | B0GAA20AA301XB23 | B0GAA20AA301 | XB23 | Raw Wtr Pmps Fltr 1 Disch MOV | Raw Water Pumps Filter 1 Discharge Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | TBD |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000013 - Raw Water | NPE7-EAI-41XX-XXX-PP-XA-007618 | NPE7-EAI-41XX-XXX-PP-XA-007636 | NPE7-EAI-41XX-XXX-IM-XA-007614 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD | To be located in the existing pumping station far away from the ERF building | A | P01 |  | 2023-03-24
RW Screening Supplier | B0GAA20AA301YB01 | B0GAA20AA301 | YB01 | Raw Wtr Pmps Fltr 1 Disch MOV | Raw Water Pumps Filter 1 Discharge Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | TBD |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000013 - Raw Water | NPE7-EAI-41XX-XXX-PP-XA-007618 | NPE7-EAI-41XX-XXX-PP-XA-007636 | NPE7-EAI-41XX-XXX-IM-XA-007614 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD | To be located in the existing pumping station far away from the ERF building | A | P01 |  | 2023-03-24
RW Screening Supplier | B0GAA20AA301YB02 | B0GAA20AA301 | YB02 | Raw Wtr Pmps Fltr 1 Disch MOV | Raw Water Pumps Filter 1 Discharge Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | TBD |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000013 - Raw Water | NPE7-EAI-41XX-XXX-PP-XA-007618 | NPE7-EAI-41XX-XXX-PP-XA-007636 | NPE7-EAI-41XX-XXX-IM-XA-007614 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD | To be located in the existing pumping station far away from the ERF building | A | P01 |  | 2023-03-24
RW Screening Supplier | B0GAA20AA302XB01 | B0GAA20AA302 | XB01 | Raw Wtr Pmps Fltr 2 Disch MOV | Raw Water Pumps Filter 2 Discharge Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | TBD |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000013 - Raw Water | NPE7-EAI-41XX-XXX-PP-XA-007618 | NPE7-EAI-41XX-XXX-PP-XA-007636 | NPE7-EAI-41XX-XXX-IM-XA-007614 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD | To be located in the existing pumping station far away from the ERF building | A | P01 |  | 2023-03-24
RW Screening Supplier | B0GAA20AA302XB02 | B0GAA20AA302 | XB02 | Raw Wtr Pmps Fltr 2 Disch MOV | Raw Water Pumps Filter 2 Discharge Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | TBD |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000013 - Raw Water | NPE7-EAI-41XX-XXX-PP-XA-007618 | NPE7-EAI-41XX-XXX-PP-XA-007636 | NPE7-EAI-41XX-XXX-IM-XA-007614 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD | To be located in the existing pumping station far away from the ERF building | A | P01 |  | 2023-03-24
RW Screening Supplier | B0GAA20AA302XB07 | B0GAA20AA302 | XB07 | Raw Wtr Pmps Fltr 2 Disch MOV | Raw Water Pumps Filter 2 Discharge Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | TBD |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000013 - Raw Water | NPE7-EAI-41XX-XXX-PP-XA-007618 | NPE7-EAI-41XX-XXX-PP-XA-007636 | NPE7-EAI-41XX-XXX-IM-XA-007614 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD | To be located in the existing pumping station far away from the ERF building | A | P01 |  | 2023-03-24
RW Screening Supplier | B0GAA20AA302XB23 | B0GAA20AA302 | XB23 | Raw Wtr Pmps Fltr 2 Disch MOV | Raw Water Pumps Filter 2 Discharge Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | TBD |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000013 - Raw Water | NPE7-EAI-41XX-XXX-PP-XA-007618 | NPE7-EAI-41XX-XXX-PP-XA-007636 | NPE7-EAI-41XX-XXX-IM-XA-007614 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD | To be located in the existing pumping station far away from the ERF building | A | P01 |  | 2023-03-24
RW Screening Supplier | B0GAA20AA302YB01 | B0GAA20AA302 | YB01 | Raw Wtr Pmps Fltr 2 Disch MOV | Raw Water Pumps Filter 2 Discharge Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | TBD |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000013 - Raw Water | NPE7-EAI-41XX-XXX-PP-XA-007618 | NPE7-EAI-41XX-XXX-PP-XA-007636 | NPE7-EAI-41XX-XXX-IM-XA-007614 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD | To be located in the existing pumping station far away from the ERF building | A | P01 |  | 2023-03-24
RW Screening Supplier | B0GAA20AA302YB02 | B0GAA20AA302 | YB02 | Raw Wtr Pmps Fltr 2 Disch MOV | Raw Water Pumps Filter 2 Discharge Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | TBD |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000013 - Raw Water | NPE7-EAI-41XX-XXX-PP-XA-007618 | NPE7-EAI-41XX-XXX-PP-XA-007636 | NPE7-EAI-41XX-XXX-IM-XA-007614 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD | To be located in the existing pumping station far away from the ERF building | A | P01 |  | 2023-03-24
EA-I&C | B0GAA20CL001XQ01 | B0GAA20CL001 | XQ01 | Waste Container Lvl | Waste Container Level | N/A | N/A |  |  | AI | 4-20mA | S |  |  | TBD |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000013 - Raw Water | NPE7-EAI-41XX-XXX-PP-XA-007618 | NPE7-EAI-41XX-XXX-PP-XA-007636 | NPE7-EAI-41XX-XXX-IM-XA-007614 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD | To be located in the existing pumping station far away from the ERF building | A | P01 |  | 2023-03-24
EA-I&C | B0GAA20CP001XQ01 | B0GAA20CP001 | XQ01 | Raw Wtr Pmps Disch Press | Raw Water Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | TBD |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000013 - Raw Water | NPE7-EAI-41XX-XXX-PP-XA-007618 | NPE7-EAI-41XX-XXX-PP-XA-007636 | NPE7-EAI-41XX-XXX-IM-XA-007614 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD | To be located in the existing pumping station far away from the ERF building | A | P01 |  | 2023-03-24
RW Screening Supplier | B0GAA20CP002XQ01 | B0GAA20CP002 | XQ01 | Raw Wtr Pmps Disch Fltr DP 1 | Raw Water Pumps Discharge Filter Differential Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | TBD |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000013 - Raw Water | NPE7-EAI-41XX-XXX-PP-XA-007618 | NPE7-EAI-41XX-XXX-PP-XA-007636 | NPE7-EAI-41XX-XXX-IM-XA-007614 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD | To be located in the existing pumping station far away from the ERF building | A | P01 |  | 2023-03-24
RW Screening Supplier | B0GAA20CP003XQ01 | B0GAA20CP003 | XQ01 | Raw Wtr Pmps Disch Fltr DP 2 | Raw Water Pumps Discharge Filter Differential Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | TBD |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000013 - Raw Water | NPE7-EAI-41XX-XXX-PP-XA-007618 | NPE7-EAI-41XX-XXX-PP-XA-007636 | NPE7-EAI-41XX-XXX-IM-XA-007614 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD | To be located in the existing pumping station far away from the ERF building | A | P01 |  | 2023-03-24
EA-I&C | B0GAA30CL001XQ01 | B0GAA30CL001 | XQ01 | Waste Collection Canal Lvl | Waste Collection Canal Level | N/A | N/A |  |  | AI | 4-20mA | S |  |  | TBD |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000013 - Raw Water | NPE7-EAI-41XX-XXX-PP-XA-007618 | NPE7-EAI-41XX-XXX-PP-XA-007636 | NPE7-EAI-41XX-XXX-IM-XA-007614 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD | To be located in the existing pumping station far away from the ERF building | A | P01 |  | 2023-03-24
WTP | B0GH_00GH001XB01 | B0GH_00GH001 | XB01 | WTP Interface: WTA started | Water Treatment Plant Interface: WTA started | WTA started |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000022 - Water Treatment Plant | NPE7-EAI-41XX-XXX-PP-XA-007609 | NPE7-EAI-41XX-XXX-PP-XA-007628 | NPE7-EAI-41XX-XXX-IM-XA-007609 | Water Treatment Plant | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
WTP | B0GH_00GH001XB02 | B0GH_00GH001 | XB02 | WTP Interface: WTA stopped | Water Treatment Plant Interface: WTA stopped | WTA stopped |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000022 - Water Treatment Plant | NPE7-EAI-41XX-XXX-PP-XA-007609 | NPE7-EAI-41XX-XXX-PP-XA-007628 | NPE7-EAI-41XX-XXX-IM-XA-007609 | Water Treatment Plant | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
WTP | B0GH_00GH001XB22 | B0GH_00GH001 | XB22 | WTP Interface: Remote/local control | Water Treatment Plant Interface: Remote/local control | Remote | Local |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000022 - Water Treatment Plant | NPE7-EAI-41XX-XXX-PP-XA-007609 | NPE7-EAI-41XX-XXX-PP-XA-007628 | NPE7-EAI-41XX-XXX-IM-XA-007609 | Water Treatment Plant | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
WTP | B0GH_00GH001XB31 | B0GH_00GH001 | XB31 | WTP Interface: Non urgent Alarm | Water Treatment Plant Interface: Non urgent Alarm | n Alarm | Alarm |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000022 - Water Treatment Plant | NPE7-EAI-41XX-XXX-PP-XA-007609 | NPE7-EAI-41XX-XXX-PP-XA-007628 | NPE7-EAI-41XX-XXX-IM-XA-007609 | Water Treatment Plant | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
WTP | B0GH_00GH001XB32 | B0GH_00GH001 | XB32 | WTP Interface: Urgent Alarm | Water Treatment Plant Interface: Urgent Alarm | n Alarm | Alarm |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000022 - Water Treatment Plant | NPE7-EAI-41XX-XXX-PP-XA-007609 | NPE7-EAI-41XX-XXX-PP-XA-007628 | NPE7-EAI-41XX-XXX-IM-XA-007609 | Water Treatment Plant | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
WTP | B0GH_00GH001XB33 | B0GH_00GH001 | XB33 | WTP Interface: No PLC anomaly | Water Treatment Plant Interface: No PLC anomaly | No PLC anomaly |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000022 - Water Treatment Plant | NPE7-EAI-41XX-XXX-PP-XA-007609 | NPE7-EAI-41XX-XXX-PP-XA-007628 | NPE7-EAI-41XX-XXX-IM-XA-007609 | Water Treatment Plant | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
WTP | B0GH_00GH001XB34 | B0GH_00GH001 | XB34 | WTP Interface: Trip | Water Treatment Plant Interface: Trip | n Trip | Trip |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000022 - Water Treatment Plant | NPE7-EAI-41XX-XXX-PP-XA-007609 | NPE7-EAI-41XX-XXX-PP-XA-007628 | NPE7-EAI-41XX-XXX-IM-XA-007609 | Water Treatment Plant | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
WTP | B0GH_00GH001YB01 | B0GH_00GH001 | YB01 | WTP Interface: WTA Start-up Cmd | Water Treatment Plant Interface: WTA Start-up Cmd | WTA Start-up Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000022 - Water Treatment Plant | NPE7-EAI-41XX-XXX-PP-XA-007609 | NPE7-EAI-41XX-XXX-PP-XA-007628 | NPE7-EAI-41XX-XXX-IM-XA-007609 | Water Treatment Plant | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
WTP | B0GH_00GH001YB02 | B0GH_00GH001 | YB02 | WTP Interface: WTA Shutdown Cmd | Water Treatment Plant Interface: WTA Shutdown Cmd | WTA Shutdown Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000022 - Water Treatment Plant | NPE7-EAI-41XX-XXX-PP-XA-007609 | NPE7-EAI-41XX-XXX-PP-XA-007628 | NPE7-EAI-41XX-XXX-IM-XA-007609 | Water Treatment Plant | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GHC02AA301XB01 | B0GHC02AA301 | XB01 | Demi Wtr Tnk 1 Mkup Vlv | Demineralized Water Tank 1 Make-up Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000018 - Demi Water Storage & Distribution | NPE7-EAI-41XX-XXX-PP-XA-007612 | NPE7-EAI-41XX-XXX-PP-XA-007631 | NPE7-EAI-41XX-XXX-IM-XA-007164 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GHC02AA301XB02 | B0GHC02AA301 | XB02 | Demi Wtr Tnk 1 Mkup Vlv | Demineralized Water Tank 1 Make-up Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000018 - Demi Water Storage & Distribution | NPE7-EAI-41XX-XXX-PP-XA-007612 | NPE7-EAI-41XX-XXX-PP-XA-007631 | NPE7-EAI-41XX-XXX-IM-XA-007164 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GHC02AA301YB02 | B0GHC02AA301 | YB02 | Demi Wtr Tnk 1 Mkup Vlv | Demineralized Water Tank 1 Make-up Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000018 - Demi Water Storage & Distribution | NPE7-EAI-41XX-XXX-PP-XA-007612 | NPE7-EAI-41XX-XXX-PP-XA-007631 | NPE7-EAI-41XX-XXX-IM-XA-007164 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GHC03AA301XB01 | B0GHC03AA301 | XB01 | Demi Wtr Tnk 2 Mkup Vlv | Demineralized Water Tank 2 Make-up Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000018 - Demi Water Storage & Distribution | NPE7-EAI-41XX-XXX-PP-XA-007612 | NPE7-EAI-41XX-XXX-PP-XA-007631 | NPE7-EAI-41XX-XXX-IM-XA-007164 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GHC03AA301XB02 | B0GHC03AA301 | XB02 | Demi Wtr Tnk 2 Mkup Vlv | Demineralized Water Tank 2 Make-up Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000018 - Demi Water Storage & Distribution | NPE7-EAI-41XX-XXX-PP-XA-007612 | NPE7-EAI-41XX-XXX-PP-XA-007631 | NPE7-EAI-41XX-XXX-IM-XA-007164 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GHC03AA301YB02 | B0GHC03AA301 | YB02 | Demi Wtr Tnk 2 Mkup Vlv | Demineralized Water Tank 2 Make-up Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000018 - Demi Water Storage & Distribution | NPE7-EAI-41XX-XXX-PP-XA-007612 | NPE7-EAI-41XX-XXX-PP-XA-007631 | NPE7-EAI-41XX-XXX-IM-XA-007164 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GHC10CL001AXQ01 | B0GHC10CL001A | XQ01 | Demi Wtr Tnk1 Lvl 1 | Demineralized Water Tank 1 Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000018 - Demi Water Storage & Distribution | NPE7-EAI-41XX-XXX-PP-XA-007612 | NPE7-EAI-41XX-XXX-PP-XA-007631 | NPE7-EAI-41XX-XXX-IM-XA-007164 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GHC10CL001BXQ01 | B0GHC10CL001B | XQ01 | Demi Wtr Tnk1 Lvl 2 | Demineralized Water Tank 1 Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000018 - Demi Water Storage & Distribution | NPE7-EAI-41XX-XXX-PP-XA-007612 | NPE7-EAI-41XX-XXX-PP-XA-007631 | NPE7-EAI-41XX-XXX-IM-XA-007164 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GHC15CL001AXQ01 | B0GHC15CL001A | XQ01 | Demi Wtr Tnk2 Lvl 1 | Demineralized Water Tank 2 Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000018 - Demi Water Storage & Distribution | NPE7-EAI-41XX-XXX-PP-XA-007612 | NPE7-EAI-41XX-XXX-PP-XA-007631 | NPE7-EAI-41XX-XXX-IM-XA-007164 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GHC15CL001BXQ01 | B0GHC15CL001B | XQ01 | Demi Wtr Tnk2 Lvl 2 | Demineralized Water Tank 2 Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000018 - Demi Water Storage & Distribution | NPE7-EAI-41XX-XXX-PP-XA-007612 | NPE7-EAI-41XX-XXX-PP-XA-007631 | NPE7-EAI-41XX-XXX-IM-XA-007164 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GHC16CP001XQ01 | B0GHC16CP001 | XQ01 | Demi Wtr Pmp1 Suct Fltr DP | Demi Water Pump 1 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000018 - Demi Water Storage & Distribution | NPE7-EAI-41XX-XXX-PP-XA-007612 | NPE7-EAI-41XX-XXX-PP-XA-007631 | NPE7-EAI-41XX-XXX-IM-XA-007164 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GHC17CP001XQ01 | B0GHC17CP001 | XQ01 | Demi Wtr Pmp2 Suct Fltr DP | Demi Water Pump 2 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000018 - Demi Water Storage & Distribution | NPE7-EAI-41XX-XXX-PP-XA-007612 | NPE7-EAI-41XX-XXX-PP-XA-007631 | NPE7-EAI-41XX-XXX-IM-XA-007164 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GHC18CP001XQ01 | B0GHC18CP001 | XQ01 | Demi Wtr Pmp3 Suct Fltr DP | Demi Water Pump 3 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000018 - Demi Water Storage & Distribution | NPE7-EAI-41XX-XXX-PP-XA-007612 | NPE7-EAI-41XX-XXX-PP-XA-007631 | NPE7-EAI-41XX-XXX-IM-XA-007164 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GHC19CP001XQ01 | B0GHC19CP001 | XQ01 | Demi Wtr Pmp4 Suct Fltr DP | Demi Water Pump 4 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000018 - Demi Water Storage & Distribution | NPE7-EAI-41XX-XXX-PP-XA-007612 | NPE7-EAI-41XX-XXX-PP-XA-007631 | NPE7-EAI-41XX-XXX-IM-XA-007164 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GHC20CP001XQ01 | B0GHC20CP001 | XQ01 | Demi Wtr Pmps Disch Press | Demi Water Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000018 - Demi Water Storage & Distribution | NPE7-EAI-41XX-XXX-PP-XA-007612 | NPE7-EAI-41XX-XXX-PP-XA-007631 | NPE7-EAI-41XX-XXX-IM-XA-007164 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GHC24AA401XQ13 | B0GHC24AA401 | XQ13 | Condensate supply to Cond Tnk CV | Condensate supply to Condenser Tank Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GHC24AA401YQ01 | B0GHC24AA401 | YQ01 | Condensate supply to Cond Tnk CV | Condensate supply to Condenser Tank Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GHC24AA402XQ13 | B0GHC24AA402 | XQ13 | Condensate Filling Line CV | Condensate Filling Line Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GHC24AA402YQ01 | B0GHC24AA402 | YQ01 | Condensate Filling Line CV | Condensate Filling Line Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GHC24CF001XQ01 | B0GHC24CF001 | XQ01 | Demin Wtr Mkup to Cond Tnk Flow | Demineralized Water Make-up to Condenser Tank Flow | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GKB10AA301XB01 | B0GKB10AA301 | XB01 | Potable Wtr Tnks Mkup Vlv | Potable Water Tanks Make-up Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GKB10AA301XB02 | B0GKB10AA301 | XB02 | Potable Wtr Tnks Mkup Vlv | Potable Water Tanks Make-up Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GKB10AA301YB01 | B0GKB10AA301 | YB01 | Potable Wtr Tnks Mkup Vlv | Potable Water Tanks Make-up Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GKB10CF001XQ01 | B0GKB10CF001 | XQ01 | TwnWtr Sply to Pot Wtr & WTP Flow | Town Water Supply to Potable Water & Water Treatment Plant Flow | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GKB10CL001AXQ01 | B0GKB10CL001A | XQ01 | Pot Wtr Compt 1 Lvl 1 | Potable Water Compartment 1 Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GKB10CL001BXQ01 | B0GKB10CL001B | XQ01 | Pot Wtr Compt 1 Lvl 2 | Potable Water Compartment 1 Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GKB10CL002AXQ01 | B0GKB10CL002A | XQ01 | Pot Wtr Compt 2 Lvl 1 | Potable Water Compartment 2 Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GKB10CL002BXQ01 | B0GKB10CL002B | XQ01 | Pot Wtr Compt 2 Lvl 2 | Potable Water Compartment 2 Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GKB10CP001XQ01 | B0GKB10CP001 | XQ01 | Pot Wtr Press Grp Inl Fltr DP | Potable Water Pressure Group Inlet Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GKB10CT001XQ01 | B0GKB10CT001 | XQ01 | Pot Wtr Compt 1 Temp | Potable Water Compartment 1 Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GKB10CT002XQ01 | B0GKB10CT002 | XQ01 | Pot Wtr Compt 2 Temp | Potable Water Compartment 2 Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GKB20CF001XQ01 | B0GKB20CF001 | XQ01 | TwnWtr Sply to Drkg Wtr Press Grp Flow | Town Water Supply to Drinking Water Pressure Group Flow | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GKB22CP001XQ01 | B0GKB22CP001 | XQ01 | Drkg Wtr Press Grp Inl Fltr DP | Drinking Water Pressure Group Inlet Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Pressure Group Supplier | B0GKB30BU001XB01 | B0GKB30BU001 | XB01 | Drkg Wtr Press Grp | Drinking Water Pressure Group | Pump1 Running |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Pressure Group Supplier | B0GKB30BU001XB02 | B0GKB30BU001 | XB02 | Drkg Wtr Press Grp | Drinking Water Pressure Group | Pump2 Running |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Pressure Group Supplier | B0GKB30BU001XB33 | B0GKB30BU001 | XB33 | Drkg Wtr Press Grp | Drinking Water Pressure Group | n Anomaly | Anomaly |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Pressure Group Supplier | B0GKB30BU001YB45 | B0GKB30BU001 | YB45 | Drkg Wtr Press Grp | Drinking Water Pressure Group | Start Permissive |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GKB30CP001XQ01 | B0GKB30CP001 | XQ01 | Drkg Wtr Press Grp Outl Press | Drinking Water Pressure Group Outlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Pressure Group Supplier | B0GKB60BU001XB01 | B0GKB60BU001 | XB01 | Pot Wtr Press Grp | Potable Water Pressure Group | Pump1 Running |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Pressure Group Supplier | B0GKB60BU001XB02 | B0GKB60BU001 | XB02 | Pot Wtr Press Grp | Potable Water Pressure Group | Pump2 Running |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Pressure Group Supplier | B0GKB60BU001XB03 | B0GKB60BU001 | XB03 | Pot Wtr Press Grp | Potable Water Pressure Group | Pump3 Running |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Pressure Group Supplier | B0GKB60BU001XB33 | B0GKB60BU001 | XB33 | Pot Wtr Press Grp | Potable Water Pressure Group | n Anomaly | Anomaly |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Pressure Group Supplier | B0GKB60BU001YB45 | B0GKB60BU001 | YB45 | Pot Wtr Press Grp | Potable Water Pressure Group | Start Permissive |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GKB70AA301XB01 | B0GKB70AA301 | XB01 | B1: Pot Wtr to Proc Wtr Tnk Blr IV | B1: Potable Water to Process Water Tank Boiler Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GKB70AA301XB02 | B0GKB70AA301 | XB02 | B1: Pot Wtr to Proc Wtr Tnk Blr IV | B1: Potable Water to Process Water Tank Boiler Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GKB70AA301YB02 | B0GKB70AA301 | YB02 | B1: Pot Wtr to Proc Wtr Tnk Blr IV | B1: Potable Water to Process Water Tank Boiler Isolation Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GKB70AA302XB01 | B0GKB70AA302 | XB01 | B2: Pot Wtr to Proc Wtr Tnk Blr IV | B2: Potable Water to Process Water Tank Boiler Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GKB70AA302XB02 | B0GKB70AA302 | XB02 | B2: Pot Wtr to Proc Wtr Tnk Blr IV | B2: Potable Water to Process Water Tank Boiler Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GKB70AA302YB02 | B0GKB70AA302 | YB02 | B2: Pot Wtr to Proc Wtr Tnk Blr IV | B2: Potable Water to Process Water Tank Boiler Isolation Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GKB70CP001XQ01 | B0GKB70CP001 | XQ01 | Pot Wtr Press Grp Outl Press | Potable Water Pressure Group Outlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000004 - Service & Potable Water Distribution System | NPE7-EAI-41XX-XXX-PP-XA-007613 | NPE7-EAI-41XX-XXX-PP-XA-007632 | NPE7-EAI-41XX-XXX-IM-XA-007613 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH20CL001AXQ01 | B0GMH20CL001A | XQ01 | BtmAshExt Pit Lvl 1 | Bottom Ash Extractor Pit Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH20CL001BXQ01 | B0GMH20CL001B | XQ01 | BtmAshExt Pit Lvl 2 | Bottom Ash Extractor Pit Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH20CP002XQ01 | B0GMH20CP002 | XQ01 | BtmAshExt Pit Pmps Disch Press | Bottom Ash Extractor Pit Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH30AA301XB01 | B0GMH30AA301 | XB01 | B1: BAE Pit to BAE Line 1 IV | Boiler 1: Bottom Ash Extractor Pit to Bottom Ash Extractor Line 1 Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH30AA301XB02 | B0GMH30AA301 | XB02 | B1: BAE Pit to BAE Line 1 IV | Boiler 1: Bottom Ash Extractor Pit to Bottom Ash Extractor Line 1 Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH30AA301YB01 | B0GMH30AA301 | YB01 | B1: BAE Pit to BAE Line 1 IV | Boiler 1: Bottom Ash Extractor Pit to Bottom Ash Extractor Line 1 Isolation Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH31AA301XB01 | B0GMH31AA301 | XB01 | B1: BAE Pit to BAE Line 2 IV | Boiler 1: Bottom Ash Extractor Pit to Bottom Ash Extractor Line 2 Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH31AA301XB02 | B0GMH31AA301 | XB02 | B1: BAE Pit to BAE Line 2 IV | Boiler 1: Bottom Ash Extractor Pit to Bottom Ash Extractor Line 2 Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH31AA301YB01 | B0GMH31AA301 | YB01 | B1: BAE Pit to BAE Line 2 IV | Boiler 1: Bottom Ash Extractor Pit to Bottom Ash Extractor Line 2 Isolation Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH32AA301XB01 | B0GMH32AA301 | XB01 | B2: BAE Pit to BAE Line 1 IV | Boiler 2: Bottom Ash Extractor Pit to Bottom Ash Extractor Line 1 Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH32AA301XB02 | B0GMH32AA301 | XB02 | B2: BAE Pit to BAE Line 1 IV | Boiler 2: Bottom Ash Extractor Pit to Bottom Ash Extractor Line 1 Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH32AA301YB01 | B0GMH32AA301 | YB01 | B2: BAE Pit to BAE Line 1 IV | Boiler 2: Bottom Ash Extractor Pit to Bottom Ash Extractor Line 1 Isolation Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH33AA301XB01 | B0GMH33AA301 | XB01 | B2: BAE Pit to BAE Line 2 IV | Boiler 2: Bottom Ash Extractor Pit to Bottom Ash Extractor Line 2 Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH33AA301XB02 | B0GMH33AA301 | XB02 | B2: BAE Pit to BAE Line 2 IV | Boiler 2: Bottom Ash Extractor Pit to Bottom Ash Extractor Line 2 Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH33AA301YB01 | B0GMH33AA301 | YB01 | B2: BAE Pit to BAE Line 2 IV | Boiler 2: Bottom Ash Extractor Pit to Bottom Ash Extractor Line 2 Isolation Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH40CL001AXQ01 | B0GMH40CL001A | XQ01 | IBA Bnkr Pit Lvl 1 | IBA Bunker Pit Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH40CL001BXQ01 | B0GMH40CL001B | XQ01 | IBA Bnkr Pit Lvl 2 | IBA Bunker Pit Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH40CP002XQ01 | B0GMH40CP002 | XQ01 | IBA Bnkr Pit Pmps Disch Press | IBA Bunker Pit Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH60CL001AXQ01 | B0GMH60CL001A | XQ01 | Blr WstWtr Pit 1 Lvl 1 | Boiler Waste Water Pit 1 Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH60CL001BXQ01 | B0GMH60CL001B | XQ01 | Blr WstWtr Pit 1 Lvl 2 | Boiler Waste Water Pit 1 Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH60CP001XQ01 | B0GMH60CP001 | XQ01 | Blr WstWtr Pit 1 Pmps Disch Press | Boiler Waste Water Pit 1 Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH60CT001XQ01 | B0GMH60CT001 | XQ01 | Blr WstWtr Pit 1 Temp | Boiler Waste Water Pit 1 Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH60CT002XQ01 | B0GMH60CT002 | XQ01 | Blr WstWtr Pit 1 Pmps Disch Temp | Boiler Waste Water Pit 1 Pumps Discharge Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH70CL001AXQ01 | B0GMH70CL001A | XQ01 | Blr WstWtr Pit 2 Lvl 1 | Boiler Waste Water Pit 2 Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH70CL001BXQ01 | B0GMH70CL001B | XQ01 | Blr WstWtr Pit 2 Lvl 2 | Boiler Waste Water Pit 2 Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH70CP001XQ01 | B0GMH70CP001 | XQ01 | Blr WstWtr Pit 2 Pmps Disch Press | Boiler Waste Water Pit 2 Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH70CT001XQ01 | B0GMH70CT001 | XQ01 | Blr WstWtr Pit 2 Temp | Boiler Waste Water Pit 2 Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH70CT002XQ01 | B0GMH70CT002 | XQ01 | Blr WstWtr Pit 2 Pmps Disch Temp | Boiler Waste Water Pit 2 Pumps Discharge Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH80AA301XB01 | B0GMH80AA301 | XB01 | B1: Blr WstWtr to BAE Line 1 IV | Boiler 1: Boiler Waste Water to Bottom Ash Extractor Line 1 Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH80AA301XB02 | B0GMH80AA301 | XB02 | B1: Blr WstWtr to BAE Line 1 IV | Boiler 1: Boiler Waste Water to Bottom Ash Extractor Line 1 Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH80AA301YB01 | B0GMH80AA301 | YB01 | B1: Blr WstWtr to BAE Line 1 IV | Boiler 1: Boiler Waste Water to Bottom Ash Extractor Line 1 Isolation Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH81AA301XB01 | B0GMH81AA301 | XB01 | B1: Blr WstWtr to BAE Line 2 IV | Boiler 1: Boiler Waste Water to Bottom Ash Extractor Line 2 Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH81AA301XB02 | B0GMH81AA301 | XB02 | B1: Blr WstWtr to BAE Line 2 IV | Boiler 1: Boiler Waste Water to Bottom Ash Extractor Line 2 Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH81AA301YB01 | B0GMH81AA301 | YB01 | B1: Blr WstWtr to BAE Line 2 IV | Boiler 1: Boiler Waste Water to Bottom Ash Extractor Line 2 Isolation Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH82AA301XB01 | B0GMH82AA301 | XB01 | B2: Blr WstWtr to BAE Line 1 IV | Boiler 2: Boiler Waste Water to Bottom Ash Extractor Line 1 Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH82AA301XB02 | B0GMH82AA301 | XB02 | B2: Blr WstWtr to BAE Line 1 IV | Boiler 2: Boiler Waste Water to Bottom Ash Extractor Line 1 Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH82AA301YB01 | B0GMH82AA301 | YB01 | B2: Blr WstWtr to BAE Line 1 IV | Boiler 2: Boiler Waste Water to Bottom Ash Extractor Line 1 Isolation Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH83AA301XB01 | B0GMH83AA301 | XB01 | B2: Blr WstWtr to BAE Line 2 IV | Boiler 2: Boiler Waste Water to Bottom Ash Extractor Line 2 Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH83AA301XB02 | B0GMH83AA301 | XB02 | B2: Blr WstWtr to BAE Line 2 IV | Boiler 2: Boiler Waste Water to Bottom Ash Extractor Line 2 Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GMH83AA301YB01 | B0GMH83AA301 | YB01 | B2: Blr WstWtr to BAE Line 2 IV | Boiler 2: Boiler Waste Water to Bottom Ash Extractor Line 2 Isolation Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GRB10CL001AXQ01 | B0GRB10CL001A | XQ01 | Sewage Pit Lvl 1 | Sewage Pit Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GRB10CL001BXQ01 | B0GRB10CL001B | XQ01 | Sewage Pit Lvl 2 | Sewage Pit Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GRB13CP001XQ01 | B0GRB13CP001 | XQ01 | Sewage Pmps Disch Press | Sewage Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GUA10CL001AXQ01 | B0GUA10CL001A | XQ01 | Rain Wtr Pit Lvl 1 | Rain Water Pit Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GUA10CL001BXQ01 | B0GUA10CL001B | XQ01 | Rain Wtr Pit Lvl 2 | Rain Water Pit Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GUA10CL002AXQ01 | B0GUA10CL002A | XQ01 | Reused Rain Wtr Tnk Lvl 1 | Reused Rain Water Tank Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GUA10CL002BXQ01 | B0GUA10CL002B | XQ01 | Reused Rain Wtr Tnk Lvl 2 | Reused Rain Water Tank Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GUA10CP001XQ01 | B0GUA10CP001 | XQ01 | Reused Rain Wtr Press Grp Inl Fltr DP | Reused Rain Water Pressure Group Inlet Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GUA13AA301XB01 | B0GUA13AA301 | XB01 | Rain Wtr Pmps Disch Vlv | Rain Water Pumps Discharge Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GUA13AA301XB02 | B0GUA13AA301 | XB02 | Rain Wtr Pmps Disch Vlv | Rain Water Pumps Discharge Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GUA13AA301YB01 | B0GUA13AA301 | YB01 | Rain Wtr Pmps Disch Vlv | Rain Water Pumps Discharge Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GUA13CP001XQ01 | B0GUA13CP001 | XQ01 | Rain Wtr Pmps Disch Press | Rain Water Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GUA13CP002XQ01 | B0GUA13CP002 | XQ01 | Rain Wtr Pmps Disch Fltr DP | Rain Water Pumps Discharge Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B0GUA13CQ001XQ01 | B0GUA13CQ001 | XQ01 | Rain Wtr Reused Wtr Tank Cl | Rain Water Reused Water Tank Chlorine | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Pressure Group Supplier | B0GUA20BU001XB01 | B0GUA20BU001 | XB01 | Rain Wtr Press Grp | Rain Water Pressure Group | Pump1 Running |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Pressure Group Supplier | B0GUA20BU001XB02 | B0GUA20BU001 | XB02 | Rain Wtr Press Grp | Rain Water Pressure Group | Pump2 Running |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Pressure Group Supplier | B0GUA20BU001XB33 | B0GUA20BU001 | XB33 | Rain Wtr Press Grp | Rain Water Pressure Group | n Anomaly | Anomaly |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Pressure Group Supplier | B0GUA20BU001YB45 | B0GUA20BU001 | YB45 | Rain Wtr Press Grp | Rain Water Pressure Group | Start Permissive |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GUA31AA302XB01 | B0GUA31AA302 | XB01 | Rain Wtr Pmps Disch Fltr MOV | Rain Water Pumps Discharge Filter Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GUA31AA302XB02 | B0GUA31AA302 | XB02 | Rain Wtr Pmps Disch Fltr MOV | Rain Water Pumps Discharge Filter Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GUA31AA302XB07 | B0GUA31AA302 | XB07 | Rain Wtr Pmps Disch Fltr MOV | Rain Water Pumps Discharge Filter Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GUA31AA302XB23 | B0GUA31AA302 | XB23 | Rain Wtr Pmps Disch Fltr MOV | Rain Water Pumps Discharge Filter Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GUA31AA302YB01 | B0GUA31AA302 | YB01 | Rain Wtr Pmps Disch Fltr MOV | Rain Water Pumps Discharge Filter Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GUA31AA302YB02 | B0GUA31AA302 | YB02 | Rain Wtr Pmps Disch Fltr MOV | Rain Water Pumps Discharge Filter Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GUA31CP001XQ01 | B0GUA31CP001 | XQ01 | Rain Wtr Ovrflw Pmps Disch Press | Rain Water Overflow Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GUA50CL001AXQ01 | B0GUA50CL001A | XQ01 | Surf Wtr Attenuation Pond Lvl 1 | Surface Water Attenuation Pond Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GUA50CL001BXQ01 | B0GUA50CL001B | XQ01 | Surf Wtr Attenuation Pond Lvl 2 | Surface Water Attenuation Pond Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0GUA50CP001XQ01 | B0GUA50CP001 | XQ01 | Surf Wtr Attenuation Pmps Disch Press | Surface Water Attenuation Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41MX-XXX-PD-XA-000016 - Waste Water | NPE7-EAI-41MX-XXX-PP-XA-007610 | NPE7-EAI-41MX-XXX-PP-XA-007629 | NPE7-EAI-41MX-XXX-IM-XA-007610 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Chemical Dosing Supplier | B0HTS01GH001XB31 | B0HTS01GH001 | XB31 | Caustic Soda Skid Interface | Caustic Soda Skid Interface | No General Alarm | General Alarm |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000017 - Chemical Dosing | NPE7-EAI-41XX-XXX-PP-XA-007617 | NPE7-EAI-41XX-XXX-PP-XA-007634 | NPE7-EAI-41XX-XXX-IM-XA-007615 | Chemical Dosing System | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Chemical Dosing Supplier | B0HTS01GH001XB33 | B0HTS01GH001 | XB33 | Caustic Soda Skid Interface | Caustic Soda Skid Interface | PLC n fail | PLC fail |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000017 - Chemical Dosing | NPE7-EAI-41XX-XXX-PP-XA-007617 | NPE7-EAI-41XX-XXX-PP-XA-007634 | NPE7-EAI-41XX-XXX-IM-XA-007615 | Chemical Dosing System | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAA10CL001AXQ01 | B0LAA10CL001A | XQ01 | Feedwater Tnk Level 1 | Feedwater Tank Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAA10CL001BXQ01 | B0LAA10CL001B | XQ01 | Feedwater Tnk Level 2 | Feedwater Tank Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAA10CL001CXQ01 | B0LAA10CL001C | XQ01 | Feedwater Tnk Level 3 | Feedwater tank Level 3 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | C | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAA10CP001AXQ01 | B0LAA10CP001A | XQ01 | Deaerator Press 1 | Deaerator Press 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAA10CP001BXQ01 | B0LAA10CP001B | XQ01 | Deaerator Press 2 | Deaerator Press 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAA10CT001XQ01 | B0LAA10CT001 | XQ01 | Feedwater Tnk Top Temp | Feedwater Tank Top Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAA10CT002XQ01 | B0LAA10CT002 | XQ01 | Feedwater Tnk Bottom Temp | Feedwater Tank Bottom Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAA20AA301XB01 | B0LAA20AA301 | XB01 | FW Tank Ovrflw MOV | Feedwater Tank Overflow Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAA20AA301XB02 | B0LAA20AA301 | XB02 | FW Tank Ovrflw MOV | Feedwater Tank Overflow Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAA20AA301XB07 | B0LAA20AA301 | XB07 | FW Tank Ovrflw MOV | Feedwater Tank Overflow Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAA20AA301XB23 | B0LAA20AA301 | XB23 | FW Tank Ovrflw MOV | Feedwater Tank Overflow Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAA20AA301YB01 | B0LAA20AA301 | YB01 | FW Tank Ovrflw MOV | Feedwater Tank Overflow Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAA20AA301YB02 | B0LAA20AA301 | YB02 | FW Tank Ovrflw MOV | Feedwater Tank Overflow Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAA30AA301XB01 | B0LAA30AA301 | XB01 | Deaerator Venting MOV | Deaerator Venting Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAA30AA301XB02 | B0LAA30AA301 | XB02 | Deaerator Venting MOV | Deaerator Venting Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAA30AA301XB07 | B0LAA30AA301 | XB07 | Deaerator Venting MOV | Deaerator Venting Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAA30AA301XB23 | B0LAA30AA301 | XB23 | Deaerator Venting MOV | Deaerator Venting Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAA30AA301YB01 | B0LAA30AA301 | YB01 | Deaerator Venting MOV | Deaerator Venting Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAA30AA301YB02 | B0LAA30AA301 | YB02 | Deaerator Venting MOV | Deaerator Venting Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC10CT001AXQ01 | B0LAC10CT001A | XQ01 | FW Pmps Inl Temp 1 | Feedwater Pumps Inlet Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC10CT001BXQ01 | B0LAC10CT001B | XQ01 | FW Pmps Inl Temp 2 | Feedwater Pumps Inlet Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC11CG301XG10 | B0LAC11CG301 | XG10 | FWP1 Wtr Leak Det | Feedwater Pump 1 Water Leak Detector | n Act | act |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | LS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC11CL301XG14 | B0LAC11CL301 | XG14 | FWP1 Lube Oil Tnk Lvl Sw | Feedwater Pump 1 Lube Oil Tank Level Switch | n Lo Lo |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | LS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC11CP001AXQ01 | B0LAC11CP001A | XQ01 | FWP1 Suct Fltr DP 1 | Feedwater Pump 1 Suction Filter Differential Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC11CP001BXQ01 | B0LAC11CP001B | XQ01 | FWP1 Suct Fltr DP 2 | Feedwater Pump 1 Suction Filter Differential Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC11CP002AXQ01 | B0LAC11CP002A | XQ01 | FWP1 Inl Press 1 | Feedwater Pump 1 Inlet Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC11CP002BXQ01 | B0LAC11CP002B | XQ01 | FWP1 Inl Press 2 | Feedwater Pump 1 Inlet Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC11CP010XG01 | B0LAC11CP010 | XG01 | FWP1 Cool Dif Press | Feedwater Pump 1 Cooler Differential Pressure | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | PS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC11CP301XG12 | B0LAC11CP301 | XG12 | FWP1 Lube Oil Press Sw | Feedwater Pump 1 Lube Oil Pressure Switch | n Low | Low |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | PS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC11CP304XG01 | B0LAC11CP304 | XG01 | FWP1 Lube Oil Fltr Dif Press Sw | Feedwater Pump 1 Lube Oil Filter Differential Pressure Switch | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | PS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC11CT001XQ01 | B0LAC11CT001 | XQ01 | FWP1 Mot DE Brg Temp | Feedwater Pump 1 Motor DE Bearing Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC11CT002XQ01 | B0LAC11CT002 | XQ01 | FWP1 Mot NDE Brg Temp | Feedwater Pump 1 Motor NDE Bearing Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC11CT003XQ01 | B0LAC11CT003 | XQ01 | FWP1 DE Brg Temp | Feedwater Pump 1 DE Bearing Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC11CT004XQ01 | B0LAC11CT004 | XQ01 | FWP1 NDE Brg Temp | Feedwater Pump 1 NDE Bearing Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC11CT010XG01 | B0LAC11CT010 | XG01 | FWP1 Water Cool Inlet Temp | Feedwater Pump 1 Water Cooling Inlet Temperature | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | TS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC11CT012XQ01 | B0LAC11CT012 | XQ01 | FWP1 Air Inl Temp | Feedwater Pump 1 Air Inlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC11CT013XQ01 | B0LAC11CT013 | XQ01 | FWP1 Air Outl Temp | Feedwater Pump 1 Air Outlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC11CT301XG01 | B0LAC11CT301 | XG01 | FWP1 Lube Oil Tnk Temp Sw | Feedwater Pump 1 Lube Oil Tank Temperature Switch | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | TS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC11CY001XQ01 | B0LAC11CY001 | XQ01 | FWP1 Brg Vibr NDE (X) | Feedwater Pump 1 Bearing Vibration NDE (X) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC11CY002XQ01 | B0LAC11CY002 | XQ01 | FWP1 Brg Vibr NDE (Y) | Feedwater Pump 1 Bearing Vibration NDE (Y) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC11CY003XQ01 | B0LAC11CY003 | XQ01 | FWP1 Brg Vibr DE (X) | Feedwater Pump 1 Bearing Vibration DE (X) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC11CY004XQ01 | B0LAC11CY004 | XQ01 | FWP1 Brg Vibr DE (Y) | Feedwater Pump 1 Bearing Vibration DE (Y) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC11CY005XQ01 | B0LAC11CY005 | XQ01 | FWP1 Axial Displac | Feedwater Pump 1 Axial Displacement | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC11CY006XQ01 | B0LAC11CY006 | XQ01 | FWP1 Mot Brg Vibr (X) | Feedwater Pump 1 Motor Bearing Vibration (X) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC11CY007XQ01 | B0LAC11CY007 | XQ01 | FWP1 Mot Brg Vibr (Y) | Feedwater Pump 1 Motor Bearing Vibration (Y) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC12CG301XG10 | B0LAC12CG301 | XG10 | FWP2 Wtr Leak Det | Feedwater Pump 2 Water Leak Detector | n Act | act |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | LS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC12CL301XG14 | B0LAC12CL301 | XG14 | FWP2 Lube Oil Tnk Lvl Sw | Feedwater Pump 2 Lube Oil Tank Level Switch | n Lo Lo |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | LS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC12CP001AXQ01 | B0LAC12CP001A | XQ01 | FWP2 Suct Fltr DP 1 | Feedwater Pump 2 Suction Filter Differential Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC12CP001BXQ01 | B0LAC12CP001B | XQ01 | FWP2 Suct Fltr DP 2 | Feedwater Pump 2 Suction Filter Differential Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC12CP002AXQ01 | B0LAC12CP002A | XQ01 | FWP2 Inlet Press 1 | Feedwater Pump 2 Inlter Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC12CP002BXQ01 | B0LAC12CP002B | XQ01 | FWP2 Inlet Press 2 | Feedwater Pump 2 Inlter Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC12CP010XG01 | B0LAC12CP010 | XG01 | FWP2 Cool Dif Press | Feedwater Pump 2 Cooling Differential Pressure | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | PS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC12CP301XG12 | B0LAC12CP301 | XG12 | FWP2 Lube Oil Press Sw | Feedwater Pump 2 Lube Oil Pressure Switch | n Low | Low |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | PS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC12CP304XG01 | B0LAC12CP304 | XG01 | FWP2 Lube Oil Fltr Dif Press Sw | Feedwater Pump 2 Lube Oil Filter Differential Pressure Switch | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | PS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC12CT001XQ01 | B0LAC12CT001 | XQ01 | FWP2 Mot DE Brg Temp | Feedwater Pump 2 Motor DE Bearing Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC12CT002XQ01 | B0LAC12CT002 | XQ01 | FWP2 Mot NDE Brg Temp | Feedwater Pump 2 Motor NDE Bearing Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC12CT003XQ01 | B0LAC12CT003 | XQ01 | FWP2 DE Brg Temp | Feedwater Pump 2 DE Bearing Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC12CT004XQ01 | B0LAC12CT004 | XQ01 | FWP2 NDE Brg Temp | Feedwater Pump 2 NDE Bearing Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC12CT010XG01 | B0LAC12CT010 | XG01 | FWP2 Water Cool Inlet Temp | Feedwater Pump 2 Water Cooling Inlet Temperature | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | TS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC12CT012XQ01 | B0LAC12CT012 | XQ01 | FWP2 Air Inlet Temp | Feedwater Pump 2 Air Inlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC12CT013XQ01 | B0LAC12CT013 | XQ01 | FWP2 Air Outl Temp | Feedwater Pump 2 Air Outlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC12CT301XG01 | B0LAC12CT301 | XG01 | FWP2 Lube Oil Tnk Temp Sw | Feedwater Pump 2 Lube Oil Tank Temperature Switch | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | TS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC12CY001XQ01 | B0LAC12CY001 | XQ01 | FWP2 Brg Vibr NDE (X) | Feedwater Pump 2 Bearing Vibration NDE (X) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC12CY002XQ01 | B0LAC12CY002 | XQ01 | FWP2 Brg Vibr NDE (Y) | Feedwater Pump 2 Bearing Vibration NDE (Y) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC12CY003XQ01 | B0LAC12CY003 | XQ01 | FWP2 Brg Vibr DE (X) | Feedwater Pump 2 Bearing Vibration DE (X) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC12CY004XQ01 | B0LAC12CY004 | XQ01 | FWP2 Brg Vibr DE (Y) | Feedwater Pump 2 Bearing Vibration DE (Y) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC12CY005XQ01 | B0LAC12CY005 | XQ01 | FWP2 Axial Displac | Feedwater Pump 2 Axial Displacement | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC12CY006XQ01 | B0LAC12CY006 | XQ01 | FWP2 Mot Brg Vibr (X) | Feedwater Pump 2 Motor Bearing Vibration (X) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC12CY007XQ01 | B0LAC12CY007 | XQ01 | FWP2 Mot Brg Vibr (Y) | Feedwater Pump 2 Motor Bearing Vibration (Y) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC13CG301XG10 | B0LAC13CG301 | XG10 | FWP3 Wtr Leak Det | Feedwater Pump 3 Water Leak Detector | n Act | act |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | LS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC13CL301XG14 | B0LAC13CL301 | XG14 | FWP3 Lube Oil Tnk Lvl Sw | Feedwater Pump 3 Lube Oil Tank Level Switch | n Lo Lo |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | LS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC13CP001AXQ01 | B0LAC13CP001A | XQ01 | FWP3 Suct Fltr DP 1 | Feedwater Pump 3 Suction Filter Differential Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC13CP001BXQ01 | B0LAC13CP001B | XQ01 | FWP3 Suct Fltr DP 2 | Feedwater Pump 3 Suction Filter Differential Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC13CP002AXQ01 | B0LAC13CP002A | XQ01 | FWP3 Inlet Press 1 | Feedwater Pump 3 Inlet Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC13CP002BXQ01 | B0LAC13CP002B | XQ01 | FWP3 Inlet Press 2 | Feedwater Pump 3 Inlet Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC13CP010XG01 | B0LAC13CP010 | XG01 | FWP3 Cool Dif Press | Feedwater Pump 3 Cooling Differential Pressure | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | PS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC13CP301XG12 | B0LAC13CP301 | XG12 | FWP3 Lube Oil Press Sw | Feedwater Pump 3 Lube Oil Pressure Switch | n Low | Low |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | PS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC13CP304XG01 | B0LAC13CP304 | XG01 | FWP3 Lube Oil Fltr Dif Press Sw | Feedwater Pump 3 Lube Oil Filter Pressure Switch | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | PS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC13CT001XQ01 | B0LAC13CT001 | XQ01 | FWP3 Mot DE Brg Temp | Feedwater Pump 3 Motor DE Bearing Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC13CT002XQ01 | B0LAC13CT002 | XQ01 | FWP3 Mot NDE Brg Temp | Feedwater Pump 3 Motor NDE Bearing Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC13CT003XQ01 | B0LAC13CT003 | XQ01 | FWP3 DE Brg Temp | Feedwater Pump 3 DE Bearing Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC13CT004XQ01 | B0LAC13CT004 | XQ01 | FWP3 NDE Brg Temp | Feedwater Pump 3 NDE Bearing Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC13CT010XG01 | B0LAC13CT010 | XG01 | FWP3 Water Cool Inlet Temp | Feedwater Pump 3 Water Cooling Inlet Temperature | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | TS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC13CT012XQ01 | B0LAC13CT012 | XQ01 | FWP3 Air Inlet Temp | Feedwater Pump 3 Air Inlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC13CT013XQ01 | B0LAC13CT013 | XQ01 | FWP3 Air Outl Temp | Feedwater Pump 3 Air Outlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC13CT301XG01 | B0LAC13CT301 | XG01 | FWP3 Lube Oil Tnk Temp Sw | Feedwater Pump 3 Lube Oil Tank Temperature Switch | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | TS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC13CY001XQ01 | B0LAC13CY001 | XQ01 | FWP3 Brg Vibr NDE (X) | Feedwater Pump 3 Bearing Vibration NDE (X) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC13CY002XQ01 | B0LAC13CY002 | XQ01 | FWP3 Brg Vibr NDE (Y) | Feedwater Pump 3 Bearing Vibration NDE (Y) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC13CY003XQ01 | B0LAC13CY003 | XQ01 | FWP3 Brg Vibr DE (X) | Feedwater Pump 3 Bearing Vibration DE (X) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC13CY004XQ01 | B0LAC13CY004 | XQ01 | FWP3 Brg Vibr DE (Y) | Feedwater Pump 3 Bearing Vibration DE (Y) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC13CY005XQ01 | B0LAC13CY005 | XQ01 | FWP3 Axial Displac | Feedwater Pump 3 Axial Displacement | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC13CY006XQ01 | B0LAC13CY006 | XQ01 | FWP3 Mot Brg Vibr (X) | Feedwater Pump 3 Motor Bearing Vibration (X) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
FWP Supplier | B0LAC13CY007XQ01 | B0LAC13CY007 | XQ01 | FWP3 Mot Brg Vibr (Y) | Feedwater Pump 3 Motor Bearing Vibration (Y) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC21AA301XB01 | B0LAC21AA301 | XB01 | FWP 1 Disch MOV | Feedwater Pump 1 Discharge Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC21AA301XB02 | B0LAC21AA301 | XB02 | FWP 1 Disch MOV | Feedwater Pump 1 Discharge Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC21AA301XB07 | B0LAC21AA301 | XB07 | FWP 1 Disch MOV | Feedwater Pump 1 Discharge Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC21AA301XB23 | B0LAC21AA301 | XB23 | FWP 1 Disch MOV | Feedwater Pump 1 Discharge Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC21AA301YB01 | B0LAC21AA301 | YB01 | FWP 1 Disch MOV | Feedwater Pump 1 Discharge Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC21AA301YB02 | B0LAC21AA301 | YB02 | FWP 1 Disch MOV | Feedwater Pump 1 Discharge Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC22AA301XB01 | B0LAC22AA301 | XB01 | FWP 2 Disch MOV | Feedwater Pump 2 Discharge Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC22AA301XB02 | B0LAC22AA301 | XB02 | FWP 2 Disch MOV | Feedwater Pump 2 Discharge Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC22AA301XB07 | B0LAC22AA301 | XB07 | FWP 2 Disch MOV | Feedwater Pump 2 Discharge Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC22AA301XB23 | B0LAC22AA301 | XB23 | FWP 2 Disch MOV | Feedwater Pump 2 Discharge Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC22AA301YB01 | B0LAC22AA301 | YB01 | FWP 2 Disch MOV | Feedwater Pump 2 Discharge Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC22AA301YB02 | B0LAC22AA301 | YB02 | FWP 2 Disch MOV | Feedwater Pump 2 Discharge Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC23AA301XB01 | B0LAC23AA301 | XB01 | FWP 3 Disch MOV | Feedwater Pump 3 Discharge Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC23AA301XB02 | B0LAC23AA301 | XB02 | FWP 3 Disch MOV | Feedwater Pump 3 Discharge Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC23AA301XB07 | B0LAC23AA301 | XB07 | FWP 3 Disch MOV | Feedwater Pump 3 Discharge Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC23AA301XB23 | B0LAC23AA301 | XB23 | FWP 3 Disch MOV | Feedwater Pump 3 Discharge Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC23AA301YB01 | B0LAC23AA301 | YB01 | FWP 3 Disch MOV | Feedwater Pump 3 Discharge Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC23AA301YB02 | B0LAC23AA301 | YB02 | FWP 3 Disch MOV | Feedwater Pump 3 Discharge Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC40CF001AXQ01 | B0LAC40CF001A | XQ01 | FW Pmps HP Disch Flow 1 | Feedwater Pumps High Pressure Discharge Flow 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC40CF001BXQ01 | B0LAC40CF001B | XQ01 | FW Pmps HP Disch Flow 2 | Feedwater Pumps High Pressure Discharge Flow 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC40CP001AXQ01 | B0LAC40CP001A | XQ01 | FW Pmps HP Disch Press 1 | Feedwater Pumps High Pressure Discharge Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC40CP001BXQ01 | B0LAC40CP001B | XQ01 | FW Pmps HP Disch Press 2 | Feedwater Pumps High Pressure Discharge Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAC40CT001XQ01 | B0LAC40CT001 | XQ01 | FW Pumps HP Disch Temp | Feedwater Pumps High Pressure Discharge Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF30CF001AXQ01 | B0LAF30CF001A | XQ01 | FW Pmps IP Disch Flow 1 | Feedwater Pumps Intermediate Pressure Discharge Flow 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF30CF001BXQ01 | B0LAF30CF001B | XQ01 | FW Pmps IP Disch Flow 2 | Feedwater Pumps Intermediate Pressure Discharge Flow 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF30CP001XQ01 | B0LAF30CP001 | XQ01 | FW Pmps IP Disch Press | Feedwater Pumps Intermediate Pressure Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF30CT001AXQ01 | B0LAF30CT001A | XQ01 | FW Pmps IP Disch Temp 1 | Feedwater Pumps Intermediate Pressure Discharge Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF30CT001BXQ01 | B0LAF30CT001B | XQ01 | FW Pmps IP Disch Temp 2 | Feedwater Pumps Intermediate Pressure Discharge Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF32AA301XB01 | B0LAF32AA301 | XB01 | Dist Heat Attemp CV Water IV | District Heating Attemperation Control Valve Water Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF32AA301XB02 | B0LAF32AA301 | XB02 | Dist Heat Attemp CV Water IV | District Heating Attemperation Control Valve Water Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF32AA301YB01 | B0LAF32AA301 | YB01 | Dist Heat Attemp CV Water IV | District Heating Attemperation Control Valve Water Isolation Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF32AA401XQ13 | B0LAF32AA401 | XQ13 | Dist Heat Attemp CV Water CV | District Heating Attemperation Control Valve Water Isolation Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF32AA401YQ01 | B0LAF32AA401 | YQ01 | Dist Heat Attemp CV Water CV | District Heating Attemperation Control Valve Water Isolation Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF32CP001XQ01 | B0LAF32CP001 | XQ01 | Dist Heat Attemp CV Wtr CV Inl Press | District Heating Attemperation Control Valve Water Control Valve Inlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF32CP002XQ01 | B0LAF32CP002 | XQ01 | Dist Heat Attemp CV Wtr CV Outl Press | District Heating Attemperation Control Valve Water Control Valve Outlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF33AA301XB01 | B0LAF33AA301 | XB01 | MS Attemp CV Water IV | Main Steam Attemperation Control Valve Water Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF33AA301XB02 | B0LAF33AA301 | XB02 | MS Attemp CV Water IV | Main Steam Attemperation Control Valve Water Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF33AA301YB01 | B0LAF33AA301 | YB01 | MS Attemp CV Water IV | Main Steam Attemperation Control Valve Water Isolation Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF33AA401XQ13 | B0LAF33AA401 | XQ13 | MS Attemp CV Water CV | Main Steam Attemperation Control Valve Water Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF33AA401YQ01 | B0LAF33AA401 | YQ01 | MS Attemp CV Water CV | Main Steam Attemperation Control Valve Water Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF33CP001XQ01 | B0LAF33CP001 | XQ01 | MS Attemp CV Water CV Inl Press | Main Steam Attemperation Control Valve Water Control Valve Inlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF33CP002XQ01 | B0LAF33CP002 | XQ01 | MS Attemp CV Water CV Outl Press | Main Steam Attemperation Control Valve Water Control Valve Outlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF34AA301XB01 | B0LAF34AA301 | XB01 | IV Extn Condtng CV Water IV | IV Extraction Conditioning Control Valve Water Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF34AA301XB02 | B0LAF34AA301 | XB02 | IV Extn Condtng CV Water IV | IV Extraction Conditioning Control Valve Water Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF34AA301YB01 | B0LAF34AA301 | YB01 | IV Extn Condtng CV Water IV | IV Extraction Conditioning Control Valve Water Isolation Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF34AA401XQ13 | B0LAF34AA401 | XQ13 | IV Extn Condtng CV Water CV | IV Extraction Conditioning Control Valve Water Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF34AA401YQ01 | B0LAF34AA401 | YQ01 | IV Extn Condtng CV Water CV | IV Extraction Conditioning Control Valve Water Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF34CP001XQ01 | B0LAF34CP001 | XQ01 | IV Extn Condtng CV Wtr CV Inl Press | IV Extraction Conditioning Control Valve Water Control Valve Inlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF34CP002XQ01 | B0LAF34CP002 | XQ01 | IV Extn Condtng CV Wtr CV Outl Press | IV Extraction Conditioning Control Valve Water Control Valve Outlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF35AA301XB01 | B0LAF35AA301 | XB01 | Ejctr Attemp CV Water IV | Ejector Attemperation Control Valve Water Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF35AA301XB02 | B0LAF35AA301 | XB02 | Ejctr Attemp CV Water IV | Ejector Attemperation Control Valve Water Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF35AA301YB01 | B0LAF35AA301 | YB01 | Ejctr Attemp CV Water IV | Ejector Attemperation Control Valve Water Isolation Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF35AA401XQ13 | B0LAF35AA401 | XQ13 | Ejctr Attemp CV Water CV | Ejector Attemperation Control Valve Water Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF35AA401YQ01 | B0LAF35AA401 | YQ01 | Ejctr Attemp CV Water CV | Ejector Attemperation Control Valve Water Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF35CP002XQ01 | B0LAF35CP002 | XQ01 | Ejctr Attemp CV Wtr CV Inl Press | Ejector Attemperation Control Valve Water Inlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LAF35CP004XQ01 | B0LAF35CP004 | XQ01 | Ejctr Attemp CV Wtr CV Outl Press | Ejector Attemperation Control Valve Water Outlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA10AA301XB01 | B0LBA10AA301 | XB01 | MS to HP ST Vent MOV | Main Steam to High Pressure Steam Turbine Vent Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA10AA301XB02 | B0LBA10AA301 | XB02 | MS to HP ST Vent MOV | Main Steam to High Pressure Steam Turbine Vent Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA10AA301XB07 | B0LBA10AA301 | XB07 | MS to HP ST Vent MOV | Main Steam to High Pressure Steam Turbine Vent Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA10AA301XB23 | B0LBA10AA301 | XB23 | MS to HP ST Vent MOV | Main Steam to High Pressure Steam Turbine Vent Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA10AA301YB01 | B0LBA10AA301 | YB01 | MS to HP ST Vent MOV | Main Steam to High Pressure Steam Turbine Vent Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA10AA301YB02 | B0LBA10AA301 | YB02 | MS to HP ST Vent MOV | Main Steam to High Pressure Steam Turbine Vent Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA10AA302XB01 | B0LBA10AA302 | XB01 | MS to ST Pot B0LBA10 Drn MOV | Main Steam to Steam Turbine Pot B0LBA10 Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA10AA302XB02 | B0LBA10AA302 | XB02 | MS to ST Pot B0LBA10 Drn MOV | Main Steam to Steam Turbine Pot B0LBA10 Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA10AA302XB07 | B0LBA10AA302 | XB07 | MS to ST Pot B0LBA10 Drn MOV | Main Steam to Steam Turbine Pot B0LBA10 Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA10AA302XB23 | B0LBA10AA302 | XB23 | MS to ST Pot B0LBA10 Drn MOV | Main Steam to Steam Turbine Pot B0LBA10 Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA10AA302XQ13 | B0LBA10AA302 | XQ13 | MS to ST Pot B0LBA10 Drn MOV | Main Steam to Steam Turbine Pot B0LBA10 Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA10AA302YB01 | B0LBA10AA302 | YB01 | MS to ST Pot B0LBA10 Drn MOV | Main Steam to Steam Turbine Pot B0LBA10 Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA10AA302YB02 | B0LBA10AA302 | YB02 | MS to ST Pot B0LBA10 Drn MOV | Main Steam to Steam Turbine Pot B0LBA10 Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA10CP002XQ01 | B0LBA10CP002 | XQ01 | MS to ST Inl Press | Main Steam to Steam Turbine Inlet Press | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA10CT002XQ01 | B0LBA10CT002 | XQ01 | MS to ST Inl Temp | Main Steam to Steam Turbine Inlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA10CT003XQ01 | B0LBA10CT003 | XQ01 | MS to ST Pot B0LBA10 Temp | Main Steam to Steam Turbine Pot B0LBA10 Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA301XB01 | B0LBA30AA301 | XB01 | B1: MS to AuxStm Isol MOV | B1: Main Steam to Auxiliary Steam Isolation Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA301XB02 | B0LBA30AA301 | XB02 | B1: MS to AuxStm Isol MOV | B1: Main Steam to Auxiliary Steam Isolation Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA301XB07 | B0LBA30AA301 | XB07 | B1: MS to AuxStm Isol MOV | B1: Main Steam to Auxiliary Steam Isolation Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA301XB23 | B0LBA30AA301 | XB23 | B1: MS to AuxStm Isol MOV | B1: Main Steam to Auxiliary Steam Isolation Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA301YB01 | B0LBA30AA301 | YB01 | B1: MS to AuxStm Isol MOV | B1: Main Steam to Auxiliary Steam Isolation Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA301YB02 | B0LBA30AA301 | YB02 | B1: MS to AuxStm Isol MOV | B1: Main Steam to Auxiliary Steam Isolation Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA302XB01 | B0LBA30AA302 | XB01 | B2: MS to Aux Steam Isol MOV | B2: Main Steam to Auxiliary Steam Isolation Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA302XB02 | B0LBA30AA302 | XB02 | B2: MS to Aux Steam Isol MOV | B2: Main Steam to Auxiliary Steam Isolation Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA302XB07 | B0LBA30AA302 | XB07 | B2: MS to Aux Steam Isol MOV | B2: Main Steam to Auxiliary Steam Isolation Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA302XB23 | B0LBA30AA302 | XB23 | B2: MS to Aux Steam Isol MOV | B2: Main Steam to Auxiliary Steam Isolation Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA302YB01 | B0LBA30AA302 | YB01 | B2: MS to Aux Steam Isol MOV | B2: Main Steam to Auxiliary Steam Isolation Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA302YB02 | B0LBA30AA302 | YB02 | B2: MS to Aux Steam Isol MOV | B2: Main Steam to Auxiliary Steam Isolation Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA303XB01 | B0LBA30AA303 | XB01 | MS Attemp CV Pot B0LBA30#1 Drn MOV | Main Steam Attemperation Control Valve Pot B0LBA30#1 Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA303XB02 | B0LBA30AA303 | XB02 | MS Attemp CV Pot B0LBA30#1 Drn MOV | Main Steam Attemperation Control Valve Pot B0LBA30#1 Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA303XB07 | B0LBA30AA303 | XB07 | MS Attemp CV Pot B0LBA30#1 Drn MOV | Main Steam Attemperation Control Valve Pot B0LBA30#1 Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA303XB23 | B0LBA30AA303 | XB23 | MS Attemp CV Pot B0LBA30#1 Drn MOV | Main Steam Attemperation Control Valve Pot B0LBA30#1 Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA303XQ13 | B0LBA30AA303 | XQ13 | MS Attemp CV Pot B0LBA30#1 Drn MOV | Main Steam Attemperation Control Valve Pot B0LBA30#1 Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA303YB01 | B0LBA30AA303 | YB01 | MS Attemp CV Pot B0LBA30#1 Drn MOV | Main Steam Attemperation Control Valve Pot B0LBA30#1 Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA303YB02 | B0LBA30AA303 | YB02 | MS Attemp CV Pot B0LBA30#1 Drn MOV | Main Steam Attemperation Control Valve Pot B0LBA30#1 Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA304XB01 | B0LBA30AA304 | XB01 | MS Attemp CV Pot B0LBA30#2 Drn MOV | Main Steam Attemperation Control Valve Pot B0LBA30#2 Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA304XB02 | B0LBA30AA304 | XB02 | MS Attemp CV Pot B0LBA30#2 Drn MOV | Main Steam Attemperation Control Valve Pot B0LBA30#2 Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA304XB07 | B0LBA30AA304 | XB07 | MS Attemp CV Pot B0LBA30#2 Drn MOV | Main Steam Attemperation Control Valve Pot B0LBA30#2 Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA304XB23 | B0LBA30AA304 | XB23 | MS Attemp CV Pot B0LBA30#2 Drn MOV | Main Steam Attemperation Control Valve Pot B0LBA30#2 Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA304XQ13 | B0LBA30AA304 | XQ13 | MS Attemp CV Pot B0LBA30#2 Drn MOV | Main Steam Attemperation Control Valve Pot B0LBA30#2 Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA304YB01 | B0LBA30AA304 | YB01 | MS Attemp CV Pot B0LBA30#2 Drn MOV | Main Steam Attemperation Control Valve Pot B0LBA30#2 Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA304YB02 | B0LBA30AA304 | YB02 | MS Attemp CV Pot B0LBA30#2 Drn MOV | Main Steam Attemperation Control Valve Pot B0LBA30#2 Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA401XQ13 | B0LBA30AA401 | XQ13 | Main Steam Attemperation CV | Main Steam Attemperation Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30AA401YQ01 | B0LBA30AA401 | YQ01 | Main Steam Attemperation CV | Main Steam Attemperation Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30CT004XQ01 | B0LBA30CT004 | XQ01 | MS Attemp CV Pot B0LBA30#1 Temp | Main Steam Attemperation Control Valve Pot B0LBA30#1 Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA30CT005XQ01 | B0LBA30CT005 | XQ01 | MS Attemp CV Pot B0LBA30#2 Temp | Main Steam Attemperation Control Valve Pot B0LBA30#2 Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA31AA302XB01 | B0LBA31AA302 | XB01 | Dist Heat Pot B0LBA31#1 Drn MOV | District Heating Pot B0LBA31#1 Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA31AA302XB02 | B0LBA31AA302 | XB02 | Dist Heat Pot B0LBA31#1 Drn MOV | District Heating Pot B0LBA31#1 Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA31AA302XB07 | B0LBA31AA302 | XB07 | Dist Heat Pot B0LBA31#1 Drn MOV | District Heating Pot B0LBA31#1 Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA31AA302XB23 | B0LBA31AA302 | XB23 | Dist Heat Pot B0LBA31#1 Drn MOV | District Heating Pot B0LBA31#1 Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA31AA302XQ13 | B0LBA31AA302 | XQ13 | Dist Heat Pot B0LBA31#1 Drn MOV | District Heating Pot B0LBA31#1 Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA31AA302YB01 | B0LBA31AA302 | YB01 | Dist Heat Pot B0LBA31#1 Drn MOV | District Heating Pot B0LBA31#1 Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA31AA302YB02 | B0LBA31AA302 | YB02 | Dist Heat Pot B0LBA31#1 Drn MOV | District Heating Pot B0LBA31#1 Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA31AA303XB01 | B0LBA31AA303 | XB01 | Dist Heat Pot B0LBA31#2 Drn MOV | District Heating Pot B0LBA31#2 Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA31AA303XB02 | B0LBA31AA303 | XB02 | Dist Heat Pot B0LBA31#2 Drn MOV | District Heating Pot B0LBA31#2 Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA31AA303XB07 | B0LBA31AA303 | XB07 | Dist Heat Pot B0LBA31#2 Drn MOV | District Heating Pot B0LBA31#2 Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA31AA303XB23 | B0LBA31AA303 | XB23 | Dist Heat Pot B0LBA31#2 Drn MOV | District Heating Pot B0LBA31#2 Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA31AA303XQ13 | B0LBA31AA303 | XQ13 | Dist Heat Pot B0LBA31#2 Drn MOV | District Heating Pot B0LBA31#2 Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA31AA303YB01 | B0LBA31AA303 | YB01 | Dist Heat Pot B0LBA31#2 Drn MOV | District Heating Pot B0LBA31#2 Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA31AA303YB02 | B0LBA31AA303 | YB02 | Dist Heat Pot B0LBA31#2 Drn MOV | District Heating Pot B0LBA31#2 Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA31AA401XQ13 | B0LBA31AA401 | XQ13 | District Heating Attemp CV | District Heating Attemperation Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA31AA401YQ01 | B0LBA31AA401 | YQ01 | District Heating Attemp CV | District Heating Attemperation Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA31CP002XQ01 | B0LBA31CP002 | XQ01 | Dist Heat Attemp CV Inl Press | District Heating Attemperation Control Valve Inlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA31CT003XQ01 | B0LBA31CT003 | XQ01 | Dist Heat Attemp CV Inl Temp | District Heating Attemperation Control Valve Inlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA31CT004XQ01 | B0LBA31CT004 | XQ01 | Dist Heat Pot B0LBA31#1 Temp | District Heating Pot B0LBA31#1 Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA31CT005XQ01 | B0LBA31CT005 | XQ01 | Dist Heat Pot B0LBA31#2 Temp | District Heating Pot B0LBA31#2 Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA40AA301XB01 | B0LBA40AA301 | XB01 | Ejctr Attemp Pot B0LBA40#1 Drn MOV | Ejector Attemperation Pot B0LBA40#1 Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA40AA301XB02 | B0LBA40AA301 | XB02 | Ejctr Attemp Pot B0LBA40#1 Drn MOV | Ejector Attemperation Pot B0LBA40#1 Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA40AA301XB07 | B0LBA40AA301 | XB07 | Ejctr Attemp Pot B0LBA40#1 Drn MOV | Ejector Attemperation Pot B0LBA40#1 Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA40AA301XB23 | B0LBA40AA301 | XB23 | Ejctr Attemp Pot B0LBA40#1 Drn MOV | Ejector Attemperation Pot B0LBA40#1 Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA40AA301XQ13 | B0LBA40AA301 | XQ13 | Ejctr Attemp Pot B0LBA40#1 Drn MOV | Ejector Attemperation Pot B0LBA40#1 Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA40AA301YB01 | B0LBA40AA301 | YB01 | Ejctr Attemp Pot B0LBA40#1 Drn MOV | Ejector Attemperation Pot B0LBA40#1 Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA40AA301YB02 | B0LBA40AA301 | YB02 | Ejctr Attemp Pot B0LBA40#1 Drn MOV | Ejector Attemperation Pot B0LBA40#1 Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA40AA302XB01 | B0LBA40AA302 | XB01 | Ejctr Attemp Pot B0LBA40#2 Drn MOV | Ejector Attemperation Pot B0LBA40#2 Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA40AA302XB02 | B0LBA40AA302 | XB02 | Ejctr Attemp Pot B0LBA40#2 Drn MOV | Ejector Attemperation Pot B0LBA40#2 Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA40AA302XB07 | B0LBA40AA302 | XB07 | Ejctr Attemp Pot B0LBA40#2 Drn MOV | Ejector Attemperation Pot B0LBA40#2 Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA40AA302XB23 | B0LBA40AA302 | XB23 | Ejctr Attemp Pot B0LBA40#2 Drn MOV | Ejector Attemperation Pot B0LBA40#2 Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA40AA302XQ13 | B0LBA40AA302 | XQ13 | Ejctr Attemp Pot B0LBA40#2 Drn MOV | Ejector Attemperation Pot B0LBA40#2 Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA40AA302YB01 | B0LBA40AA302 | YB01 | Ejctr Attemp Pot B0LBA40#2 Drn MOV | Ejector Attemperation Pot B0LBA40#2 Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA40AA302YB02 | B0LBA40AA302 | YB02 | Ejctr Attemp Pot B0LBA40#2 Drn MOV | Ejector Attemperation Pot B0LBA40#2 Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA40CT001XQ01 | B0LBA40CT001 | XQ01 | Ejctr Attemp Pot B0LBA40#1 Temp | Ejector Attemperation Pot B0LBA40#1 Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA40CT002XQ01 | B0LBA40CT002 | XQ01 | Ejctr Attemp Pot B0LBA40#2 Temp | Ejector Attemperation Pot B0LBA40#2 Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA50AA401XQ13 | B0LBA50AA401 | XQ13 | Ejectors Attemperation | Ejectors Attemperation | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBA50AA401YQ01 | B0LBA50AA401 | YQ01 | Ejectors Attemperation | Ejectors Attemperation | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA303XB01 | B0LBD10AA303 | XB01 | MP Extn IV Pot B0LBD10#1 Drn MOV | MP Extraction Isolation Valve Pot B0LBD10#1 Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA303XB02 | B0LBD10AA303 | XB02 | MP Extn IV Pot B0LBD10#1 Drn MOV | MP Extraction Isolation Valve Pot B0LBD10#1 Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA303XB07 | B0LBD10AA303 | XB07 | MP Extn IV Pot B0LBD10#1 Drn MOV | MP Extraction Isolation Valve Pot B0LBD10#1 Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA303XB23 | B0LBD10AA303 | XB23 | MP Extn IV Pot B0LBD10#1 Drn MOV | MP Extraction Isolation Valve Pot B0LBD10#1 Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA303XQ13 | B0LBD10AA303 | XQ13 | MP Extn IV Pot B0LBD10#1 Drn MOV | MP Extraction Isolation Valve Pot B0LBD10#1 Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA303YB01 | B0LBD10AA303 | YB01 | MP Extn IV Pot B0LBD10#1 Drn MOV | MP Extraction Isolation Valve Pot B0LBD10#1 Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA303YB02 | B0LBD10AA303 | YB02 | MP Extn IV Pot B0LBD10#1 Drn MOV | MP Extraction Isolation Valve Pot B0LBD10#1 Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA304XB01 | B0LBD10AA304 | XB01 | IV Extn Pot B0LBD10#2 Drn CV | Isolation Valve Extraction Pot B0LBD10#2 Drain Control Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA304XB02 | B0LBD10AA304 | XB02 | IV Extn Pot B0LBD10#2 Drn CV | Isolation Valve Extraction Pot B0LBD10#2 Drain Control Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA304XB07 | B0LBD10AA304 | XB07 | IV Extn Pot B0LBD10#2 Drn CV | Isolation Valve Extraction Pot B0LBD10#2 Drain Control Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA304XB23 | B0LBD10AA304 | XB23 | IV Extn Pot B0LBD10#2 Drn CV | Isolation Valve Extraction Pot B0LBD10#2 Drain Control Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA304XQ13 | B0LBD10AA304 | XQ13 | IV Extn Pot B0LBD10#2 Drn CV | Isolation Valve Extraction Pot B0LBD10#2 Drain Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA304YB01 | B0LBD10AA304 | YB01 | IV Extn Pot B0LBD10#2 Drn CV | Isolation Valve Extraction Pot B0LBD10#2 Drain Control Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA304YB02 | B0LBD10AA304 | YB02 | IV Extn Pot B0LBD10#2 Drn CV | Isolation Valve Extraction Pot B0LBD10#2 Drain Control Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA305XB01 | B0LBD10AA305 | XB01 | IV Extn Pot B0LBD10#3 Drn CV | Isolation Valve Extraction Pot B0LBD10#3 Drain Control Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA305XB02 | B0LBD10AA305 | XB02 | IV Extn Pot B0LBD10#3 Drn CV | Isolation Valve Extraction Pot B0LBD10#3 Drain Control Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA305XB07 | B0LBD10AA305 | XB07 | IV Extn Pot B0LBD10#3 Drn CV | Isolation Valve Extraction Pot B0LBD10#3 Drain Control Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA305XB23 | B0LBD10AA305 | XB23 | IV Extn Pot B0LBD10#3 Drn CV | Isolation Valve Extraction Pot B0LBD10#3 Drain Control Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA305XQ13 | B0LBD10AA305 | XQ13 | IV Extn Pot B0LBD10#3 Drn CV | Isolation Valve Extraction Pot B0LBD10#3 Drain Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA305YB01 | B0LBD10AA305 | YB01 | IV Extn Pot B0LBD10#3 Drn CV | Isolation Valve Extraction Pot B0LBD10#3 Drain Control Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA305YB02 | B0LBD10AA305 | YB02 | IV Extn Pot B0LBD10#3 Drn CV | Isolation Valve Extraction Pot B0LBD10#3 Drain Control Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA401XQ13 | B0LBD10AA401 | XQ13 | IV Extraction Conditioning CV | Isolation Valve Extraction Conditioning Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10AA401YQ01 | B0LBD10AA401 | YQ01 | IV Extraction Conditioning CV | Isolation Valve Extraction Conditioning Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10CP001XQ01 | B0LBD10CP001 | XQ01 | MP Extn IV Press | MP Extraction Isolation Valve Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10CP002XQ01 | B0LBD10CP002 | XQ01 | IV Extn Stm to Condtng CV Press | Isolation Valve Extraction Steam to Conditioning Control Valve Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10CT001XQ01 | B0LBD10CT001 | XQ01 | MP Extn IV Temp | MP Extraction Isolation Valve Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10CT002XQ01 | B0LBD10CT002 | XQ01 | MP Extn IV Pot B0LBD10#1 Temp | MP Extraction Isolation Valve Pot B0LBD10#1 Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10CT003XQ01 | B0LBD10CT003 | XQ01 | IV Extn Stm to Condtng CV Temp | Isolation Valve Extraction Steam to Conditioning Control Valve Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10CT004XQ01 | B0LBD10CT004 | XQ01 | IV Extn Pot B0LBD10#2 Temp | Isolation Valve Extraction Pot B0LBD10#2 Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD10CT005XQ01 | B0LBD10CT005 | XQ01 | IV Extn Pot B0LBD10#3 Temp | Isolation Valve Extraction Pot B0LBD10#3 Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD20AA303XB01 | B0LBD20AA303 | XB01 | MP Extn III Pot B0LBD20 Drn MOV | MP Extraction III Pot B0LBD20 Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD20AA303XB02 | B0LBD20AA303 | XB02 | MP Extn III Pot B0LBD20 Drn MOV | MP Extraction III Pot B0LBD20 Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD20AA303XB07 | B0LBD20AA303 | XB07 | MP Extn III Pot B0LBD20 Drn MOV | MP Extraction III Pot B0LBD20 Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD20AA303XB23 | B0LBD20AA303 | XB23 | MP Extn III Pot B0LBD20 Drn MOV | MP Extraction III Pot B0LBD20 Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD20AA303XQ13 | B0LBD20AA303 | XQ13 | MP Extn III Pot B0LBD20 Drn MOV | MP Extraction III Pot B0LBD20 Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD20AA303YB01 | B0LBD20AA303 | YB01 | MP Extn III Pot B0LBD20 Drn MOV | MP Extraction III Pot B0LBD20 Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD20AA303YB02 | B0LBD20AA303 | YB02 | MP Extn III Pot B0LBD20 Drn MOV | MP Extraction III Pot B0LBD20 Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD20CP001XQ01 | B0LBD20CP001 | XQ01 | MP Extn III Press | MP Extraction III Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD20CT001XQ01 | B0LBD20CT001 | XQ01 | MP Extn III Temp | MP Extraction III Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBD20CT002XQ01 | B0LBD20CT002 | XQ01 | MP Extn III Pot B0LBD20 Temp | MP Extraction III Pot B0LBD20 Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG10AA301XB01 | B0LBG10AA301 | XB01 | AuxStm Hdr Pot B0LBG10 Drn MOV | Auxiliary Steam Header Pot B0LBG10 Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG10AA301XB02 | B0LBG10AA301 | XB02 | AuxStm Hdr Pot B0LBG10 Drn MOV | Auxiliary Steam Header Pot B0LBG10 Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG10AA301XB07 | B0LBG10AA301 | XB07 | AuxStm Hdr Pot B0LBG10 Drn MOV | Auxiliary Steam Header Pot B0LBG10 Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG10AA301XB23 | B0LBG10AA301 | XB23 | AuxStm Hdr Pot B0LBG10 Drn MOV | Auxiliary Steam Header Pot B0LBG10 Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG10AA301YB01 | B0LBG10AA301 | YB01 | AuxStm Hdr Pot B0LBG10 Drn MOV | Auxiliary Steam Header Pot B0LBG10 Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG10AA301YB02 | B0LBG10AA301 | YB02 | AuxStm Hdr Pot B0LBG10 Drn MOV | Auxiliary Steam Header Pot B0LBG10 Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG10CP001AXQ01 | B0LBG10CP001A | XQ01 | AuxStm Hdr Press 1 | Auxiliary Steam Header Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG10CP001BXQ01 | B0LBG10CP001B | XQ01 | AuxStm Hdr Press 2 | Auxiliary Steam Header Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG10CT001AXQ01 | B0LBG10CT001A | XQ01 | AuxStm Hdr Temp 1 | Auxiliary Steam Header Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG10CT001BXQ01 | B0LBG10CT001B | XQ01 | AuxStm Hdr Temp 2 | Auxiliary Steam Header Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG10CT004XQ01 | B0LBG10CT004 | XQ01 | AuxStm Hdr Pot B0LBG10 Temp | Auxiliary Steam Header Pot B0LBG10 Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG11CP001AXQ01 | B0LBG11CP001A | XQ01 | IV Extn Condtng CV Outl Press 1 | Isolation Valve Extraction Conditioning Control Valve Outlet Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG11CP001BXQ01 | B0LBG11CP001B | XQ01 | IV Extn Condtng CV Outl Press 2 | Isolation Valve Extraction Conditioning Control Valve Outlet Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG11CT001AXQ01 | B0LBG11CT001A | XQ01 | IV Extn Condtng CV Outl Temp 1 | Isolation Valve Extraction Conditioning Control Valve Outlet Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG11CT001BXQ01 | B0LBG11CT001B | XQ01 | IV Extn Condtng CV Outl Temp 2 | Isolation Valve Extraction Conditioning Control Valve Outlet Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG12CP001AXQ01 | B0LBG12CP001A | XQ01 | MS Attemp CV Outl Press 1 | Main Steam Attemperation Control Valve Outlet Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG12CP001BXQ01 | B0LBG12CP001B | XQ01 | MS Attemp CV Outl Press 2 | Main Steam Attemperation Control Valve Outlet Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG12CT001AXQ01 | B0LBG12CT001A | XQ01 | MS Attemp CV Outl Temp 1 | Main Steam Attemperation Control Valve Outlet Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG12CT001BXQ01 | B0LBG12CT001B | XQ01 | MS Attemp CV Outl Temp 2 | Main Steam Attemperation Control Valve Outlet Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG20AA301XB01 | B0LBG20AA301 | XB01 | AuxStm to Deaer Byp MOV | Auxiliary Steam to Deaerator By-pass Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG20AA301XB02 | B0LBG20AA301 | XB02 | AuxStm to Deaer Byp MOV | Auxiliary Steam to Deaerator By-pass Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG20AA301XB07 | B0LBG20AA301 | XB07 | AuxStm to Deaer Byp MOV | Auxiliary Steam to Deaerator By-pass Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG20AA301XB23 | B0LBG20AA301 | XB23 | AuxStm to Deaer Byp MOV | Auxiliary Steam to Deaerator By-pass Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG20AA301XQ13 | B0LBG20AA301 | XQ13 | AuxStm to Deaer Byp MOV | Auxiliary Steam to Deaerator By-pass Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG20AA301YB01 | B0LBG20AA301 | YB01 | AuxStm to Deaer Byp MOV | Auxiliary Steam to Deaerator By-pass Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG20AA301YB02 | B0LBG20AA301 | YB02 | AuxStm to Deaer Byp MOV | Auxiliary Steam to Deaerator By-pass Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG20AA302XB01 | B0LBG20AA302 | XB01 | AuxStm to Deaer Pot B0LBG20 Drn MOV | Auxiliary Steam to Deaerator Pot B0LBG20 Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG20AA302XB02 | B0LBG20AA302 | XB02 | AuxStm to Deaer Pot B0LBG20 Drn MOV | Auxiliary Steam to Deaerator Pot B0LBG20 Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG20AA302XB07 | B0LBG20AA302 | XB07 | AuxStm to Deaer Pot B0LBG20 Drn MOV | Auxiliary Steam to Deaerator Pot B0LBG20 Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG20AA302XB23 | B0LBG20AA302 | XB23 | AuxStm to Deaer Pot B0LBG20 Drn MOV | Auxiliary Steam to Deaerator Pot B0LBG20 Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG20AA302XQ13 | B0LBG20AA302 | XQ13 | AuxStm to Deaer Pot B0LBG20 Drn MOV | Auxiliary Steam to Deaerator Pot B0LBG20 Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG20AA302YB01 | B0LBG20AA302 | YB01 | AuxStm to Deaer Pot B0LBG20 Drn MOV | Auxiliary Steam to Deaerator Pot B0LBG20 Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG20AA302YB02 | B0LBG20AA302 | YB02 | AuxStm to Deaer Pot B0LBG20 Drn MOV | Auxiliary Steam to Deaerator Pot B0LBG20 Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG20AA401XQ13 | B0LBG20AA401 | XQ13 | AuxStm to Deaer CV | Auxiliary Steam to Deaerator Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG20AA401YQ01 | B0LBG20AA401 | YQ01 | AuxStm to Deaer CV | Auxiliary Steam to Deaerator Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG20CT001XQ01 | B0LBG20CT001 | XQ01 | AuxStm to Deaer Pot B0LBG20 Temp | Auxiliary Steam to Deaerator Pot B0LBG20 Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG30AA301XB01 | B0LBG30AA301 | XB01 | AuxStm to AirPrehtr Pot Drn MOV | Auxiliary Steam to Air Preheater Pot Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG30AA301XB02 | B0LBG30AA301 | XB02 | AuxStm to AirPrehtr Pot Drn MOV | Auxiliary Steam to Air Preheater Pot Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG30AA301XB07 | B0LBG30AA301 | XB07 | AuxStm to AirPrehtr Pot Drn MOV | Auxiliary Steam to Air Preheater Pot Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG30AA301XB23 | B0LBG30AA301 | XB23 | AuxStm to AirPrehtr Pot Drn MOV | Auxiliary Steam to Air Preheater Pot Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG30AA301XQ13 | B0LBG30AA301 | XQ13 | AuxStm to AirPrehtr Pot Drn MOV | Auxiliary Steam to Air Preheater Pot Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG30AA301YB01 | B0LBG30AA301 | YB01 | AuxStm to AirPrehtr Pot Drn MOV | Auxiliary Steam to Air Preheater Pot Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG30AA301YB02 | B0LBG30AA301 | YB02 | AuxStm to AirPrehtr Pot Drn MOV | Auxiliary Steam to Air Preheater Pot Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG30CP001AXQ01 | B0LBG30CP001A | XQ01 | AuxStm to AirPreHtrs Press 1 | Auxiliary Steam to Air Preheater Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG30CP001BXQ01 | B0LBG30CP001B | XQ01 | AuxStm to AirPreHtrs Press 2 | Auxiliary Steam to Air Preheater Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG30CT001XQ01 | B0LBG30CT001 | XQ01 | AuxStm to AirPrehtr Drn Temp | Auxiliary Steam to Air Preheater Drain Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG40CP001AXQ01 | B0LBG40CP001A | XQ01 | Dist Heat Attemp CV Outl Press 1 | District Heating Attemperation Control Valve Outlet Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG40CP001BXQ01 | B0LBG40CP001B | XQ01 | Dist Heat Attemp CV Outl Press 2 | District Heating Attemperation Control Valve Outlet Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG40CT001AXQ01 | B0LBG40CT001A | XQ01 | Dist Heat Attemp CV Outl Temp 1 | District Heating Attemperation Control Valve Outlet Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG40CT001BXQ01 | B0LBG40CT001B | XQ01 | Dist Heat Attemp CV Outl Temp 2 | District Heating Attemperation Control Valve Outlet Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG50AA301XB01 | B0LBG50AA301 | XB01 | Ejctr Attemp Pot B0LBG50 Drn MOV | Ejector Attemperation Pot B0LBG50 Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG50AA301XB02 | B0LBG50AA301 | XB02 | Ejctr Attemp Pot B0LBG50 Drn MOV | Ejector Attemperation Pot B0LBG50 Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG50AA301XB07 | B0LBG50AA301 | XB07 | Ejctr Attemp Pot B0LBG50 Drn MOV | Ejector Attemperation Pot B0LBG50 Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG50AA301XB23 | B0LBG50AA301 | XB23 | Ejctr Attemp Pot B0LBG50 Drn MOV | Ejector Attemperation Pot B0LBG50 Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG50AA301XQ13 | B0LBG50AA301 | XQ13 | Ejctr Attemp Pot B0LBG50 Drn MOV | Ejector Attemperation Pot B0LBG50 Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG50AA301YB01 | B0LBG50AA301 | YB01 | Ejctr Attemp Pot B0LBG50 Drn MOV | Ejector Attemperation Pot B0LBG50 Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG50AA301YB02 | B0LBG50AA301 | YB02 | Ejctr Attemp Pot B0LBG50 Drn MOV | Ejector Attemperation Pot B0LBG50 Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG50CP001AXQ01 | B0LBG50CP001A | XQ01 | Ejctr Attemp CV Outl Press 1 | Ejector Attemperation Control Valve Outlet Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG50CP001BXQ01 | B0LBG50CP001B | XQ01 | Ejctr Attemp CV Outl Press 2 | Ejector Attemperation Control Valve Outlet Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG50CT001AXQ01 | B0LBG50CT001A | XQ01 | Ejctr Attemp CV Outl Temp 1 | Ejector Attemperation Control Valve Outlet Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG50CT001BXQ01 | B0LBG50CT001B | XQ01 | Ejctr Attemp CV Outl Temp 2 | Ejector Attemperation Control Valve Outlet Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBG50CT002XQ01 | B0LBG50CT002 | XQ01 | Ejctr Attemp Pot B0LBG50 Temp | Ejector Attemperation Pot B0LBG50 Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS10AA303XB01 | B0LBS10AA303 | XB01 | LP Extn II Pot B0LBS10 Drn Vlv | LP Extraction II Pot B0LBS10 Drain Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS10AA303XB02 | B0LBS10AA303 | XB02 | LP Extn II Pot B0LBS10 Drn Vlv | LP Extraction II Pot B0LBS10 Drain Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS10AA303YB01 | B0LBS10AA303 | YB01 | LP Extn II Pot B0LBS10 Drn Vlv | LP Extraction II Pot B0LBS10 Drain Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS10AA304XB01 | B0LBS10AA304 | XB01 | Stm to District Htg Exchr Pot MOV | Steam to District Heating Exchanger Pot Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS10AA304XB02 | B0LBS10AA304 | XB02 | Stm to District Htg Exchr Pot MOV | Steam to District Heating Exchanger Pot Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS10AA304XB07 | B0LBS10AA304 | XB07 | Stm to District Htg Exchr Pot MOV | Steam to District Heating Exchanger Pot Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS10AA304XB23 | B0LBS10AA304 | XB23 | Stm to District Htg Exchr Pot MOV | Steam to District Heating Exchanger Pot Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS10AA304YB01 | B0LBS10AA304 | YB01 | Stm to District Htg Exchr Pot MOV | Steam to District Heating Exchanger Pot Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS10AA304YB02 | B0LBS10AA304 | YB02 | Stm to District Htg Exchr Pot MOV | Steam to District Heating Exchanger Pot Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS10AA401XQ13 | B0LBS10AA401 | XQ13 | Stm to District Htg Exchr Inl CV1 | Steam to District Heating Exchanger Inlet Control Valve 1 | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS10AA401YQ01 | B0LBS10AA401 | YQ01 | Stm to District Htg Exchr Inl CV1 | Steam to District Heating Exchanger Inlet Control Valve 1 | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS10AA402XQ13 | B0LBS10AA402 | XQ13 | Stm to District Htg Exchr Inl CV2 | Steam to District Heating Exchanger Inlet Control Valve 2 | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS10AA402YQ01 | B0LBS10AA402 | YQ01 | Stm to District Htg Exchr Inl CV2 | Steam to District Heating Exchanger Inlet Control Valve 2 | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS10CL001XG01 | B0LBS10CL001 | XG01 | LP Extn II Pot B0LBS10 Lvl Sw | LP Extraction II Pot B0LBS10 Level Switch | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | LS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS10CL002XG01 | B0LBS10CL002 | XG01 | LP Extn II Pot B0LBS10 Lvl Sw | LP Extraction II Pot B0LBS10 Level Switch | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | LS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS10CL301XG01 | B0LBS10CL301 | XG01 | Stm to District Htg Exchr Pot Lvl Sw | Steam to District Heating Exchanger Potable Level Switch | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | LS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS10CL302XG01 | B0LBS10CL302 | XG01 | Stm to District Htg Exchr Pot Lvl Sw | Steam to District Heating Exchanger Potable Level Switch | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | LS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS10CP001XQ01 | B0LBS10CP001 | XQ01 | LP Extn II Press | LP Extraction II Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS10CP002XQ01 | B0LBS10CP002 | XQ01 | LP Extn II Hdr Press | LP Extraction II Header Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS10CT001XQ01 | B0LBS10CT001 | XQ01 | LP Extn II Temp | LP Extraction II Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS10CT002XQ01 | B0LBS10CT002 | XQ01 | LP Extn II Hdr Temp | LP Extraction II Header Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS20AA303XB01 | B0LBS20AA303 | XB01 | LP Extn I Pot B0LBS20 Drn Vlv | LP Extraction I Pot B0LBS20 Drain Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS20AA303XB02 | B0LBS20AA303 | XB02 | LP Extn I Pot B0LBS20 Drn Vlv | LP Extraction I Pot B0LBS20 Drain Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS20AA303YB01 | B0LBS20AA303 | YB01 | LP Extn I Pot B0LBS20 Drn Vlv | LP Extraction I Pot B0LBS20 Drain Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS20CL001XG01 | B0LBS20CL001 | XG01 | LP Extn I to Expan Drain Tnk Lvl Sw 1 | LP Extraction I to Expansion Drain Tank Level Switch 1 | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | LS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS20CL002XG01 | B0LBS20CL002 | XG01 | LP Extn I to Expan Drain Tnk Lvl Sw 2 | LP Extraction I to Expansion Drain Tank Level Switch 2 | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | LS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS20CP001XQ01 | B0LBS20CP001 | XQ01 | LP Extn I Press | LP Extraction I Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS20CP002XQ01 | B0LBS20CP002 | XQ01 | MS to LP Prehtr Press | Main Steam to LP Preheater Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS20CT001XQ01 | B0LBS20CT001 | XQ01 | LP Extn I Temp | LP Extraction I Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBS20CT005XQ01 | B0LBS20CT005 | XQ01 | MS to LP Prehtr Temp | Main Steam to LP Preheater Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBW10AA301XB01 | B0LBW10AA301 | XB01 | MS to ST Sl Pot B0LBW10 Drn MOV | Main Steam to Steam Turbine Seal Pot B0LBW10 Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBW10AA301XB02 | B0LBW10AA301 | XB02 | MS to ST Sl Pot B0LBW10 Drn MOV | Main Steam to Steam Turbine Seal Pot B0LBW10 Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBW10AA301XB07 | B0LBW10AA301 | XB07 | MS to ST Sl Pot B0LBW10 Drn MOV | Main Steam to Steam Turbine Seal Pot B0LBW10 Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBW10AA301XB23 | B0LBW10AA301 | XB23 | MS to ST Sl Pot B0LBW10 Drn MOV | Main Steam to Steam Turbine Seal Pot B0LBW10 Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBW10AA301XQ13 | B0LBW10AA301 | XQ13 | MS to ST Sl Pot B0LBW10 Drn MOV | Main Steam to Steam Turbine Seal Pot B0LBW10 Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBW10AA301YB01 | B0LBW10AA301 | YB01 | MS to ST Sl Pot B0LBW10 Drn MOV | Main Steam to Steam Turbine Seal Pot B0LBW10 Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBW10AA301YB02 | B0LBW10AA301 | YB02 | MS to ST Sl Pot B0LBW10 Drn MOV | Main Steam to Steam Turbine Seal Pot B0LBW10 Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBW10CP001XQ01 | B0LBW10CP001 | XQ01 | MS to ST Seal Inl Press | Main Steam to Steam Turbine Seal Inlet Press | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBW10CT001XQ01 | B0LBW10CT001 | XQ01 | MS to ST Seal Inl Temp | Main Steam to Steam Turbine Seal Inlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LBW10CT002XQ01 | B0LBW10CT002 | XQ01 | MS to ST Sl Pot B0LBW10 Temp | Main Steam to Steam Turbine Seal Pot B0LBW10 Temp | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
ACC Supplier | B0LCA10CL001AXQ01 | B0LCA10CL001A | XQ01 | Condensate Tank Lvl 1 | Condensate Tank Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
ACC Supplier | B0LCA10CL001BXQ01 | B0LCA10CL001B | XQ01 | Condensate Tank Lvl 1 | Condensate Tank Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
ACC Supplier | B0LCA10CL001CXQ01 | B0LCA10CL001C | XQ01 | Condensate Tank Lvl 1 | Condensate Tank Level 3 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA11AA001XB01 | B0LCA11AA001 | XB01 | CP1 Suct Mnl Vlv | Condensate Pump 1 Suction Manual Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA11AA001XB02 | B0LCA11AA001 | XB02 | CP1 Suct Mnl Vlv | Condensate Pump 1 Suction Manual Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA11CG301XG10 | B0LCA11CG301 | XG10 | CP1 Wtr Leak Det | Condensate Pump 1 Water Leak Detector | n Act | act |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | LS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA11CP001XQ01 | B0LCA11CP001 | XQ01 | CP1 Suct Fltr DP | Condensate Pump 1 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA11CP002XQ01 | B0LCA11CP002 | XQ01 | CP1 Suct Press | Condensate Pump 1 Suction Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA11CP017XG01 | B0LCA11CP017 | XG01 | CP1 Cool Dif Press | Condensate Pump 1 Cooling Differential Pressure | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | PS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA11CT001XQ01 | B0LCA11CT001 | XQ01 | CP1 Suct Temp | Condensate Pump 1 Suction Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA11CT010XQ01 | B0LCA11CT010 | XQ01 | CP1 Mot DE Brg Temp | Condensate Pump 1 Motor DE Bearing Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA11CT011XQ01 | B0LCA11CT011 | XQ01 | CP1 Mot NDE Brg Temp | Condensate Pump 1 Motor NDE Bearing Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA11CT012XQ01 | B0LCA11CT012 | XQ01 | CP1 DE Brg Temp | Condensate Pump 1 DE Bearing Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA11CT013XQ01 | B0LCA11CT013 | XQ01 | CP1 NDE Brg Temp | Condensate Pump 1 NDE Bearing Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA11CT014XQ01 | B0LCA11CT014 | XQ01 | CP1 Air Inlet Temp | Condensate Pump 1 Air Inlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA11CT015XQ01 | B0LCA11CT015 | XQ01 | CP1 Air Outl Temp | Condensate Pump 1 Air Outlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA11CT016XG01 | B0LCA11CT016 | XG01 | CP1 Water Cool Inlet Temp | Condensate Pump 1 Water Cooling Inlet Temperature | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | TS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA11CY001XQ01 | B0LCA11CY001 | XQ01 | CP1 Mot Brg Vibr (X) | Condensate Pump 1 Motor Bearing Vibration (X) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA11CY002XQ01 | B0LCA11CY002 | XQ01 | CP1 Mot Brg Vibr (Y) | Condensate Pump 1 Motor Bearing Vibration (Y) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA11CY003XQ01 | B0LCA11CY003 | XQ01 | CP1 Brg Vibr (X) | Condensate Pump 1 Bearing Vibration (X) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA11CY004XQ01 | B0LCA11CY004 | XQ01 | CP1 Brg Vibr (Y) | Condensate Pump 1 Bearing Vibration (Y) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA12AA001XB01 | B0LCA12AA001 | XB01 | CP2 Suct Mnl Vlv | Condensate Pump 2 Suction Manual Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA12AA001XB02 | B0LCA12AA001 | XB02 | CP2 Suct Mnl Vlv | Condensate Pump 2 Suction Manual Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA12CG301XG10 | B0LCA12CG301 | XG10 | CP2 Wtr Leak Det | Condensate Pump 2 Water Leak Detector | n Act | act |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | LS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA12CP001XQ01 | B0LCA12CP001 | XQ01 | CP2 Suct Fltr DP | Condensate Pump 2 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA12CP002XQ01 | B0LCA12CP002 | XQ01 | CP2 Suct Press | Condensate Pump 2 Suction Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA12CP017XG01 | B0LCA12CP017 | XG01 | CP2 Cool Dif Press | Condensate Pump 2 Cooling Differential Pressure | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | PS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA12CT001XQ01 | B0LCA12CT001 | XQ01 | CP2 Suct Temp | Condensate Pump 2 Suction Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA12CT010XQ01 | B0LCA12CT010 | XQ01 | CP2 Mot DE Brg Temp | Condensate Pump 2 Motor DE Bearing Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA12CT011XQ01 | B0LCA12CT011 | XQ01 | CP2 Mot NDE Brg Temp | Condensate Pump 2 Motor NDE Bearing Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA12CT012XQ01 | B0LCA12CT012 | XQ01 | CP2 DE Brg Temp | Condensate Pump 2 DE Bearing Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA12CT013XQ01 | B0LCA12CT013 | XQ01 | CP2 NDE Brg Temp | Condensate Pump 2 NDE Bearing Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA12CT014XQ01 | B0LCA12CT014 | XQ01 | CP2 Air Inlet Temp | Condensate Pump 2 Air Inlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA12CT015XQ01 | B0LCA12CT015 | XQ01 | CP2 Air Outl Temp | Condensate Pump 2 Air Outlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA12CT016XG01 | B0LCA12CT016 | XG01 | CP2 Water Cool Inlet Temp | Condensate Pump 2 Water Cooling Inlet Temperature | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | TS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA12CY001XQ01 | B0LCA12CY001 | XQ01 | CP2 Mot Brg Vibr (X) | Condensate Pump 2 Motor Bearing Vibration (X) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA12CY002XQ01 | B0LCA12CY002 | XQ01 | CP2 Mot Brg Vibr (Y) | Condensate Pump 2 Motor Bearing Vibration (Y) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA12CY003XQ01 | B0LCA12CY003 | XQ01 | CP2 Brg Vibr (X) | Condensate Pump 2 Bearing Vibration (X) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CP Supplier | B0LCA12CY004XQ01 | B0LCA12CY004 | XQ01 | CP2 Brg Vibr (Y) | Condensate Pump 2 Bearing Vibration (Y) | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | YT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA301XB01 | B0LCA20AA301 | XB01 | Conds Distr to LP Prehtr MOV | Condensate Distribution to LP Preheater Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA301XB02 | B0LCA20AA301 | XB02 | Conds Distr to LP Prehtr MOV | Condensate Distribution to LP Preheater Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA301XB07 | B0LCA20AA301 | XB07 | Conds Distr to LP Prehtr MOV | Condensate Distribution to LP Preheater Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA301XB23 | B0LCA20AA301 | XB23 | Conds Distr to LP Prehtr MOV | Condensate Distribution to LP Preheater Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA301YB01 | B0LCA20AA301 | YB01 | Conds Distr to LP Prehtr MOV | Condensate Distribution to LP Preheater Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA301YB02 | B0LCA20AA301 | YB02 | Conds Distr to LP Prehtr MOV | Condensate Distribution to LP Preheater Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA302XB01 | B0LCA20AA302 | XB01 | LP Prehtr to ScrubStg1Que MOV | LP Preheater to Scrubber Condensate Preheater Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA302XB02 | B0LCA20AA302 | XB02 | LP Prehtr to ScrubStg1Que MOV | LP Preheater to Scrubber Condensate Preheater Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA302XB07 | B0LCA20AA302 | XB07 | LP Prehtr to ScrubStg1Que MOV | LP Preheater to Scrubber Condensate Preheater Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA302XB23 | B0LCA20AA302 | XB23 | LP Prehtr to ScrubStg1Que MOV | LP Preheater to Scrubber Condensate Preheater Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA302YB01 | B0LCA20AA302 | YB01 | LP Prehtr to ScrubStg1Que MOV | LP Preheater to Scrubber Condensate Preheater Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA302YB02 | B0LCA20AA302 | YB02 | LP Prehtr to ScrubStg1Que MOV | LP Preheater to Scrubber Condensate Preheater Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA303XB01 | B0LCA20AA303 | XB01 | Conds Distr to ScrubStg1Que MOV | Condensate Distribution to Scrubber Condensate Preheater Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA303XB02 | B0LCA20AA303 | XB02 | Conds Distr to ScrubStg1Que MOV | Condensate Distribution to Scrubber Condensate Preheater Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA303XB07 | B0LCA20AA303 | XB07 | Conds Distr to ScrubStg1Que MOV | Condensate Distribution to Scrubber Condensate Preheater Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA303XB23 | B0LCA20AA303 | XB23 | Conds Distr to ScrubStg1Que MOV | Condensate Distribution to Scrubber Condensate Preheater Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA303YB01 | B0LCA20AA303 | YB01 | Conds Distr to ScrubStg1Que MOV | Condensate Distribution to Scrubber Condensate Preheater Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA303YB02 | B0LCA20AA303 | YB02 | Conds Distr to ScrubStg1Que MOV | Condensate Distribution to Scrubber Condensate Preheater Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA401XQ13 | B0LCA20AA401 | XQ13 | GSC By-pass CV | Gland Steam Condenser By-pass Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA401YQ01 | B0LCA20AA401 | YQ01 | GSC By-pass CV | Gland Steam Condenser By-pass Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA402XQ13 | B0LCA20AA402 | XQ13 | ScrubStg1Que to FW Tnk Lvl CV | Scrubber Condensate Preheater to Feedwater Tank Level Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA402YQ01 | B0LCA20AA402 | YQ01 | ScrubStg1Que to FW Tnk Lvl CV | Scrubber Condensate Preheater to Feedwater Tank Level Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA403XQ13 | B0LCA20AA403 | XQ13 | ScrubStg1Que Flow CV | Scrubber Condensate Preheater Flow Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20AA403YQ01 | B0LCA20AA403 | YQ01 | ScrubStg1Que Flow CV | Scrubber Condensate Preheater Flow Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CF001AXQ01 | B0LCA20CF001A | XQ01 | GSC to Conds Distrl Flow 1 | Gland Steam Condenser to Condensate District Flow 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CF001BXQ01 | B0LCA20CF001B | XQ01 | GSC to Conds Distrl Flow 2 | Gland Steam Condenser to Condensate District Flow 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CF002AXQ01 | B0LCA20CF002A | XQ01 | ScrubStg1Que Inl Flow 1 | Scrubber Condensate Preheater Inlet Flow 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CF002BXQ01 | B0LCA20CF002B | XQ01 | ScrubStg1Que Inl Flow 2 | Scrubber Condensate Preheater Inlet Flow 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CP001XQ01 | B0LCA20CP001 | XQ01 | Cnds Pmps Disch Press | Condenser Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CP002XQ01 | B0LCA20CP002 | XQ01 | Cnds Pmps to Vac Ejctr Condsr Fltr DP | Condenser Pumps to Vacuum Ejector Condensate Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CP003XQ01 | B0LCA20CP003 | XQ01 | Cnds Vac Ejctr Condsr Inl Press | Condenser Vacuum Ejector Condensate Inlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CP004XQ01 | B0LCA20CP004 | XQ01 | Cnds Vac Ejctr Condsr Outl Press | Condenser Vacuum Ejector Condensate Outlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CP005XQ01 | B0LCA20CP005 | XQ01 | LP Prehtr to Intmd Conds Htr Press | LP Preheater to Intermediate Condensate Heater Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CP006XQ01 | B0LCA20CP006 | XQ01 | Conds Distr to LP Prehtr Press | Condensate District to LP Preheater Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CP007XQ01 | B0LCA20CP007 | XQ01 | GSC to Conds Distr Press | Gland Steam Condenser to Condensate District Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CP008XQ01 | B0LCA20CP008 | XQ01 | ScrubStg1Que Inl Press | Scrubber Condensate Preheater Inlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CP009XQ01 | B0LCA20CP009 | XQ01 | ScrubStg1Que Outl Press | Scrubber Condensate Preheater Outlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CT001XQ01 | B0LCA20CT001 | XQ01 | Cnds Vac Ejctr Condsr Inl Temp | Condenser Vacuum Ejector Condensate Inlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CT002XQ01 | B0LCA20CT002 | XQ01 | Cnds Vac Ejctr Condsr Outl Temp | Condenser Vacuum Ejector Condensate Outlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CT003XQ01 | B0LCA20CT003 | XQ01 | GSC to Conds Distr Temp | Gland Steam Condenser to Condensate District Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CT005XQ01 | B0LCA20CT005 | XQ01 | Conds Distr to LP Prehtr Temp | Condensate District to LP Preheater Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CT006XQ01 | B0LCA20CT006 | XQ01 | ScrubStg1Que Inl Temp | Scrubber Condensate Preheater Inlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CT007XQ01 | B0LCA20CT007 | XQ01 | ScrubStg1Que Outl Temp | Scrubber Condensate Preheater Outlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CT008AXQ01 | B0LCA20CT008A | XQ01 | Cond Hdr to BlwDn Cool Temp 1 | Condensate Header to Blowdown Cooling Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CT008BXQ01 | B0LCA20CT008B | XQ01 | Cond Hdr to BlwDn Cool Temp 2 | Condensate Header to Blowdown Cooling Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CT009XQ01 | B0LCA20CT009 | XQ01 | Blwdn Cool to Cond Hdr Temp | Blowdown Cooling to Condensate Header Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA20CT010XQ01 | B0LCA20CT010 | XQ01 | LP Prehtr to Intmd Conds Htr Temp | LP Preheater to Intermediate Condensate Heater Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA23AA401XQ13 | B0LCA23AA401 | XQ13 | GSC to Blr Reused Wtr CV | Gland Steam Condenser to Boiler Reused Water Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA23AA401YQ01 | B0LCA23AA401 | YQ01 | GSC to Blr Reused Wtr CV | Gland Steam Condenser to Boiler Reused Water Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA24AA401XQ13 | B0LCA24AA401 | XQ13 | Condensate Min Flow CV | Condensate Minimum Flow Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCA24AA401YQ01 | B0LCA24AA401 | YQ01 | Condensate Min Flow CV | Condensate Minimum Flow Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC10AA301XB01 | B0LCC10AA301 | XB01 | LP Prehtr Emerg Drain MOV | LP Preheater Emergency Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC10AA301XB02 | B0LCC10AA301 | XB02 | LP Prehtr Emerg Drain MOV | LP Preheater Emergency Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC10AA301XB07 | B0LCC10AA301 | XB07 | LP Prehtr Emerg Drain MOV | LP Preheater Emergency Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC10AA301XB23 | B0LCC10AA301 | XB23 | LP Prehtr Emerg Drain MOV | LP Preheater Emergency Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC10AA301YB01 | B0LCC10AA301 | YB01 | LP Prehtr Emerg Drain MOV | LP Preheater Emergency Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC10AA301YB02 | B0LCC10AA301 | YB02 | LP Prehtr Emerg Drain MOV | LP Preheater Emergency Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC10AA401XQ13 | B0LCC10AA401 | XQ13 | LP Prehtr Emerg Drain CV | LP Preheater Emergency Drain Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC10AA401YQ01 | B0LCC10AA401 | YQ01 | LP Prehtr Emerg Drain CV | LP Preheater Emergency Drain Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC10CL001AXQ01 | B0LCC10CL001A | XQ01 | LP Prehtr Lvl 1 | LP Preheater Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC10CL001BXQ01 | B0LCC10CL001B | XQ01 | LP Prehtr Lvl 2 | LP Preheater Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC10CL001CXQ01 | B0LCC10CL001C | XQ01 | LP Prehtr Lvl 3 | LP Preheater Level 3 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | C | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC10CP001XQ01 | B0LCC10CP001 | XQ01 | LP Prehtr Press | LP Preheater Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC11CP001XQ01 | B0LCC11CP001 | XQ01 | LP Htr Drns Pmp1 Suct Fltr DP | LP Heater Drains Pump 1 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC12CP001XQ01 | B0LCC12CP001 | XQ01 | LP Htr Drns Pmp2 Suct Fltr DP | LP Heater Drains Pump 2 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC30AA401XQ13 | B0LCC30AA401 | XQ13 | LP Prehtr Normal Drain CV | LP Preheater Normal Drain Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC30AA401YQ01 | B0LCC30AA401 | YQ01 | LP Prehtr Normal Drain CV | LP Preheater Normal Drain Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC30CP001XQ01 | B0LCC30CP001 | XQ01 | LP Htr Drns Pmps Disch Press | LP Heater Drains Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC30CP002XQ01 | B0LCC30CP002 | XQ01 | LP Prehtr Dnstrm Press | LP Preheater Downstream Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC40AA302XB01 | B0LCC40AA302 | XB01 | District Htg Exchr Emerg Drn MOV | District Heating Exchanger Emergency Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC40AA302XB02 | B0LCC40AA302 | XB02 | District Htg Exchr Emerg Drn MOV | District Heating Exchanger Emergency Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC40AA302XB07 | B0LCC40AA302 | XB07 | District Htg Exchr Emerg Drn MOV | District Heating Exchanger Emergency Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC40AA302XB23 | B0LCC40AA302 | XB23 | District Htg Exchr Emerg Drn MOV | District Heating Exchanger Emergency Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC40AA302YB01 | B0LCC40AA302 | YB01 | District Htg Exchr Emerg Drn MOV | District Heating Exchanger Emergency Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC40AA302YB02 | B0LCC40AA302 | YB02 | District Htg Exchr Emerg Drn MOV | District Heating Exchanger Emergency Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC40AA401XQ13 | B0LCC40AA401 | XQ13 | District Htg Exchr Emerg Drn CV | District Heating Exchanger Emergency Drain Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC40AA401YQ01 | B0LCC40AA401 | YQ01 | District Htg Exchr Emerg Drn CV | District Heating Exchanger Emergency Drain Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC60CL001AXQ01 | B0LCC60CL001A | XQ01 | District Htg Exchr Lvl 1 | District Heating Exchanger Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC60CL001BXQ01 | B0LCC60CL001B | XQ01 | District Htg Exchr Lvl 2 | District Heating Exchanger Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC60CL001CXQ01 | B0LCC60CL001C | XQ01 | District Htg Exchr Lvl 3 | District Heating Exchanger Level 3 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | C | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC60CP001AXQ01 | B0LCC60CP001A | XQ01 | District Htg Exchr Press 1 | District Heating Exchanger Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC60CP001BXQ01 | B0LCC60CP001B | XQ01 | District Htg Exchr Press 2 | District Heating Exchanger Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC71CP001XQ01 | B0LCC71CP001 | XQ01 | District Htg Drn Pmp1 Suct Fltr DP | District Heating Drain Pump 1 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC72CP001XQ01 | B0LCC72CP001 | XQ01 | District Htg Drn Pmp2 Suct Fltr DP | District Heating Drain Pump 2 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC80AA401XQ13 | B0LCC80AA401 | XQ13 | District Htg Pmps Disch CV | District Heating Pumps Discharge Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC80AA401YQ01 | B0LCC80AA401 | YQ01 | District Htg Pmps Disch CV | District Heating Pumps Discharge Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC80CP001XQ01 | B0LCC80CP001 | XQ01 | District Htg Drn Pmps Disch Press | District Heating Drain Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCC81CF001XQ01 | B0LCC81CF001 | XQ01 | District Htg Drn Pmps Disch Flow | District Heating Drain Pumps Discharge Flow | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCE40AA301XB01 | B0LCE40AA301 | XB01 | ST Vac Exp Tnk Vent Attemp IV | Steam Turbine Vacuum Expansion Tank Vent Attemperation Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCE40AA301XB02 | B0LCE40AA301 | XB02 | ST Vac Exp Tnk Vent Attemp IV | Steam Turbine Vacuum Expansion Tank Vent Attemperation Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCE40AA301YB02 | B0LCE40AA301 | YB02 | ST Vac Exp Tnk Vent Attemp IV | Steam Turbine Vacuum Expansion Tank Vent Attemperation Isolation Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCE50AA301XB01 | B0LCE50AA301 | XB01 | Atm Flash Tnk Vent Attemp IV | Atmospheric Flash Tank Vent Attemperation Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCE50AA301XB02 | B0LCE50AA301 | XB02 | Atm Flash Tnk Vent Attemp IV | Atmospheric Flash Tank Vent Attemperation Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCE50AA301YB02 | B0LCE50AA301 | YB02 | Atm Flash Tnk Vent Attemp IV | Atmospheric Flash Tank Vent Attemperation Isolation Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCE50AA302XB01 | B0LCE50AA302 | XB01 | Atm Flash Tnk Attemp Wtr IV | Atmospheric Flash Tank Attemperation Water Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCE50AA302XB02 | B0LCE50AA302 | XB02 | Atm Flash Tnk Attemp Wtr IV | Atmospheric Flash Tank Attemperation Water Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCE50AA302YB02 | B0LCE50AA302 | YB02 | Atm Flash Tnk Attemp Wtr IV | Atmospheric Flash Tank Attemperation Water Isolation Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCM10CL001AXQ01 | B0LCM10CL001A | XQ01 | Atm Flash Tnk Lvl 1 | Atmospheric Flash Tank Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCM10CL001BXQ01 | B0LCM10CL001B | XQ01 | Atm Flash Tnk Lvl 2 | Atmospheric Flash Tank Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCM10CL301XG52 | B0LCM10CL301 | XG52 | Atm Flash Tnk Ovrflw Lvl Sw | Atmospheric Flash Tank Overflow Level Switch | low | n low |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | N/A | LS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCM10CT001XQ01 | B0LCM10CT001 | XQ01 | Atm Flash Tnk Vent Temp | Atmospheric Flash Tank Vent Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCM20CP001XQ01 | B0LCM20CP001 | XQ01 | Atm Flash Tnk Press | Atmospheric Flash Tank Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCM20CT001XQ01 | B0LCM20CT001 | XQ01 | Atm Flash Tnk Temp | Atmospheric Flash Tank Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCM21CP001XQ01 | B0LCM21CP001 | XQ01 | Atm Drn Tnk Pmp1 Suct Fltr DP | Atmospheric Drain Tank Pump 1 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCM22CP001XQ01 | B0LCM22CP001 | XQ01 | Atm Drn Tnk Pmp2 Suct Fltr DP | Atmospheric Drain Tank Pump 2 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCM30AA401XQ13 | B0LCM30AA401 | XQ13 | Atm Drn Tnk Pmps Disch to Cnds CV | Atmospheric Drain Tank Pumps Discharge to Condensate Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCM30AA401YQ01 | B0LCM30AA401 | YQ01 | Atm Drn Tnk Pmps Disch to Cnds CV | Atmospheric Drain Tank Pumps Discharge to Condensate Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCM30CP001XQ01 | B0LCM30CP001 | XQ01 | Atm Drn Tnk Pmps Disch Press | Atmospheric Drain Tank Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCM40CL001AXQ01 | B0LCM40CL001A | XQ01 | ST Vac Exp Tnk Lvl 1 | Steam Turbine Vacuum Expansion Tank Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCM40CL001BXQ01 | B0LCM40CL001B | XQ01 | ST Vac Exp Tnk Lvl 2 | Steam Turbine Vacuum Expansion Tank Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCM40CT001XQ01 | B0LCM40CT001 | XQ01 | ST Vac Exp Tnk Vent Temp | Steam Turbine Vacuum Expansion Tank Vent Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCM50CP001XQ01 | B0LCM50CP001 | XQ01 | ST Vac Exp Tnk Press | Steam Turbine Vacuum Expansion Tank Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCM51CP001XQ01 | B0LCM51CP001 | XQ01 | ST Vac Exp Tnk Pmp1 Suct Fltr DP | Steam Turbine Vacuum Expansion Tank Pump 1 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCM52CP001XQ01 | B0LCM52CP001 | XQ01 | ST Vac Exp Tnk Pmp2 Suct Fltr DP | Steam Turbine Vacuum Expansion Tank Pump 2 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCM60AA401XQ13 | B0LCM60AA401 | XQ13 | ST Vac Exp Tnk Pmps Disch to Cnds CV | Steam Turbine Vacuum Expansion Tank Pumps Discharge to Condensate Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCM60AA401YQ01 | B0LCM60AA401 | YQ01 | ST Vac Exp Tnk Pmps Disch to Cnds CV | Steam Turbine Vacuum Expansion Tank Pumps Discharge to Condensate Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCM60CP001XQ01 | B0LCM60CP001 | XQ01 | ST Vac Exp Tnk Pmps Disch Press | Steam Turbine Vacuum Expansion Tank Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000015 - Steam Turbine Drains | NPE7-EAI-41XX-XXX-PP-XA-007644 | NPE7-EAI-41XX-XXX-PP-XA-007654 | NPE7-EAI-41XX-XXX-IM-XA-007644 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCN10CL001AXQ01 | B0LCN10CL001A | XQ01 | Blr Cnd Rtn Tnk Lvl 1 | Boiler Condensate Return Tank Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCN10CL001BXQ01 | B0LCN10CL001B | XQ01 | Blr Cnd Rtn Tnk Lvl 2 | Boiler Condensate Return Tank Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCN10CP001XQ01 | B0LCN10CP001 | XQ01 | Blr Cnd Rtn Tnk Press | Boiler Condensate Return Tank Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCN10CT001AXQ01 | B0LCN10CT001A | XQ01 | Blr Cnd Rtn Pmps Suct Temp 1 | Boiler Condensate Return Pumps Suction Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCN10CT001BXQ01 | B0LCN10CT001B | XQ01 | Blr Cnd Rtn Pmps Suct Temp 2 | Boiler Condensate Return Pumps Suction Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCN11CP001AXQ01 | B0LCN11CP001A | XQ01 | Blr Cnd Rtn Pmp 1 Press 1 | Boiler Condensate Return Pmp 1 Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCN11CP001BXQ01 | B0LCN11CP001B | XQ01 | Blr Cnd Rtn Pmp 1 Press 2 | Boiler Condensate Return Pmp 1 Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCN11CP001XQ01 | B0LCN11CP001 | XQ01 | Blr Cnd Rtn Pmp 1 Suct Filtr DP 1 | Boiler Condensate Return Pmp 1 Suction Filter Differential Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCN12CP001AXQ01 | B0LCN12CP001A | XQ01 | Blr Cnd Rtn Pmp 2 Press 1 | Boiler Condensate Return Pump 2 Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCN12CP001BXQ01 | B0LCN12CP001B | XQ01 | Blr Cnd Rtn Pmp 2 Press 2 | Boiler Condensate Return Pump 2 Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCN12CP001XQ01 | B0LCN12CP001 | XQ01 | Blr Cnd Rtn Pmp 2 Suct Filtr DP 1 | Boiler Condensate Return Pump 2 Suction Filter Differential Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCN20AA401XQ13 | B0LCN20AA401 | XQ13 | Blr Cnd Rtn Pmps Disch CV | Boiler Condensate Return Pumps Discharge Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCN20AA401YQ01 | B0LCN20AA401 | YQ01 | Blr Cnd Rtn Pmps Disch CV | Boiler Condensate Return Pumps Discharge Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCN20CP001AXQ01 | B0LCN20CP001A | XQ01 | Blr Cnd Rtn Pmps Disch Press 1 | Boiler Condensate Return Pumps Discharge Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCN20CP001BXQ01 | B0LCN20CP001B | XQ01 | Blr Cnd Rtn Pmps Disch Press 2 | Boiler Condensate Return Pumps Discharge Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCN61CP001XQ01 | B0LCN61CP001 | XQ01 | LP Blr Cnd Rtn Tnk Inl Press | LP Boiler Condensate Return Tank Inlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCN61CT001XQ01 | B0LCN61CT001 | XQ01 | LP Blr Cnd Rtn Tnk Inl Temp | LP Boiler Condensate Return Tank Inlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCN70CP001XQ01 | B0LCN70CP001 | XQ01 | HP Pri AirPreHtr to Blr Cnd Rtn Tnk Inl Press | HP Primary Air Preheater to Boiler Condensate Return Tank Inlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCN70CT001XQ01 | B0LCN70CT001 | XQ01 | HP Pri AirPreHtr to Blr Cnd Rtn Tnk Inl Temp | HP Primary Air Preheater to Boiler Condensate Return Tank Inlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCN80CP001XQ01 | B0LCN80CP001 | XQ01 | HP FluGas to Blr Cnd Rtn Tnk Inl Press | HP Flue Gas to Boiler Condensate Return Tank Inlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCN80CT001XQ01 | B0LCN80CT001 | XQ01 | HP FluGas to Blr Cnd Rtn Tnk Inl Temp | HP Flue Gas to Boiler Condensate Return Tank Inlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCQ17AA301XB01 | B0LCQ17AA301 | XB01 | Emerg BlwDn to Blr Reused Wtr Tnk1 IV | Emergency Blowdown to Boiler Reused Water Tank 1 Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000006 - Boiler Reused Water System | NPE7-EAI-41AX-XXX-PP-XA-000101 | NPE7-EAI-41XX-XXX-PP-XA-007633 | NPE7-EAI-41AX-XXX-IM-XA-000101 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCQ17AA301XB02 | B0LCQ17AA301 | XB02 | Emerg BlwDn to Blr Reused Wtr Tnk1 IV | Emergency Blowdown to Boiler Reused Water Tank 1 Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000006 - Boiler Reused Water System | NPE7-EAI-41AX-XXX-PP-XA-000101 | NPE7-EAI-41XX-XXX-PP-XA-007633 | NPE7-EAI-41AX-XXX-IM-XA-000101 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCQ17AA301YB02 | B0LCQ17AA301 | YB02 | Emerg BlwDn to Blr Reused Wtr Tnk1 IV | Emergency Blowdown to Boiler Reused Water Tank 1 Isolation Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000006 - Boiler Reused Water System | NPE7-EAI-41AX-XXX-PP-XA-000101 | NPE7-EAI-41XX-XXX-PP-XA-007633 | NPE7-EAI-41AX-XXX-IM-XA-000101 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCQ17AA302XB01 | B0LCQ17AA302 | XB01 | Emerg BlwDn to Blr Reused Wtr Tnk2 IV | Emergency Blowdown to Boiler Reused Water Tank 2 Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000006 - Boiler Reused Water System | NPE7-EAI-41AX-XXX-PP-XA-000101 | NPE7-EAI-41XX-XXX-PP-XA-007633 | NPE7-EAI-41AX-XXX-IM-XA-000101 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCQ17AA302XB02 | B0LCQ17AA302 | XB02 | Emerg BlwDn to Blr Reused Wtr Tnk2 IV | Emergency Blowdown to Boiler Reused Water Tank 2 Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000006 - Boiler Reused Water System | NPE7-EAI-41AX-XXX-PP-XA-000101 | NPE7-EAI-41XX-XXX-PP-XA-007633 | NPE7-EAI-41AX-XXX-IM-XA-000101 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCQ17AA302YB02 | B0LCQ17AA302 | YB02 | Emerg BlwDn to Blr Reused Wtr Tnk2 IV | Emergency Blowdown to Boiler Reused Water Tank 2 Isolation Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000006 - Boiler Reused Water System | NPE7-EAI-41AX-XXX-PP-XA-000101 | NPE7-EAI-41XX-XXX-PP-XA-007633 | NPE7-EAI-41AX-XXX-IM-XA-000101 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCQ20CL001AXQ01 | B0LCQ20CL001A | XQ01 | Blr Reused Wtr Tnk 1 Lvl 1 | Boiler Reused Water Tank 1 Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000006 - Boiler Reused Water System | NPE7-EAI-41AX-XXX-PP-XA-000101 | NPE7-EAI-41XX-XXX-PP-XA-007633 | NPE7-EAI-41AX-XXX-IM-XA-000101 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCQ20CL001BXQ01 | B0LCQ20CL001B | XQ01 | Blr Reused Wtr Tnk 1 Lvl 2 | Boiler Reused Water Tank 1 Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000006 - Boiler Reused Water System | NPE7-EAI-41AX-XXX-PP-XA-000101 | NPE7-EAI-41XX-XXX-PP-XA-007633 | NPE7-EAI-41AX-XXX-IM-XA-000101 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCQ25CL001AXQ01 | B0LCQ25CL001A | XQ01 | Blr Reused Wtr Tnk 2 Lvl 1 | Boiler Reused Water Tank 2 Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000006 - Boiler Reused Water System | NPE7-EAI-41AX-XXX-PP-XA-000101 | NPE7-EAI-41XX-XXX-PP-XA-007633 | NPE7-EAI-41AX-XXX-IM-XA-000101 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCQ25CL001BXQ01 | B0LCQ25CL001B | XQ01 | Blr Reused Wtr Tnk 2 Lvl 2 | Boiler Reused Water Tank 2 Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000006 - Boiler Reused Water System | NPE7-EAI-41AX-XXX-PP-XA-000101 | NPE7-EAI-41XX-XXX-PP-XA-007633 | NPE7-EAI-41AX-XXX-IM-XA-000101 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCQ30AA301XB01 | B0LCQ30AA301 | XB01 | B1: BlwDn Cool to Proc Wtr Tnk Blr IV | B1: Blowdown Cooling to Process Water Tank Boiler Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCQ30AA301XB02 | B0LCQ30AA301 | XB02 | B1: BlwDn Cool to Proc Wtr Tnk Blr IV | B1: Blowdown Cooling to Process Water Tank Boiler Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCQ30AA301YB02 | B0LCQ30AA301 | YB02 | B1: BlwDn Cool to Proc Wtr Tnk Blr IV | B1: Blowdown Cooling to Process Water Tank Boiler Isolation Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCQ30AA302XB01 | B0LCQ30AA302 | XB01 | B2: BlwDn Cool to Proc Wtr Tnk Blr IV | B2: Blowdown Cooling to Process Water Tank Boiler Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCQ30AA302XB02 | B0LCQ30AA302 | XB02 | B2: BlwDn Cool to Proc Wtr Tnk Blr IV | B2: Blowdown Cooling to Process Water Tank Boiler Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCQ30AA302YB02 | B0LCQ30AA302 | YB02 | B2: BlwDn Cool to Proc Wtr Tnk Blr IV | B2: Blowdown Cooling to Process Water Tank Boiler Isolation Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCQ30CT001XQ01 | B0LCQ30CT001 | XQ01 | Blwdn Cool to Proc Wtr Tanks Temp | Blowdown Cooling to Process Water Tanks Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCQ31CP001XQ01 | B0LCQ31CP001 | XQ01 | Blr Reused Wtr Pmp1 Suct Fltr DP | Boiler Reused Water Pump 1 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000006 - Boiler Reused Water System | NPE7-EAI-41AX-XXX-PP-XA-000101 | NPE7-EAI-41XX-XXX-PP-XA-007633 | NPE7-EAI-41AX-XXX-IM-XA-000101 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCQ32CP001XQ01 | B0LCQ32CP001 | XQ01 | Blr Reused Wtr Pmp2 Suct Fltr DP | Boiler Reused Water Pump 2 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000006 - Boiler Reused Water System | NPE7-EAI-41AX-XXX-PP-XA-000101 | NPE7-EAI-41XX-XXX-PP-XA-007633 | NPE7-EAI-41AX-XXX-IM-XA-000101 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0LCQ40CP001XQ01 | B0LCQ40CP001 | XQ01 | Blr Reused Wtr Pmps Disch Press | Boiler Reused Water Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000006 - Boiler Reused Water System | NPE7-EAI-41AX-XXX-PP-XA-000101 | NPE7-EAI-41XX-XXX-PP-XA-007633 | NPE7-EAI-41AX-XXX-IM-XA-000101 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFA10AA301XB01 | B0NFA10AA301 | XB01 | District Htg Exchr Fd Byp MOV | District Heating Exchanger Feed By-pass Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFA10AA301XB02 | B0NFA10AA301 | XB02 | District Htg Exchr Fd Byp MOV | District Heating Exchanger Feed By-pass Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFA10AA301XB07 | B0NFA10AA301 | XB07 | District Htg Exchr Fd Byp MOV | District Heating Exchanger Feed By-pass Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFA10AA301XB23 | B0NFA10AA301 | XB23 | District Htg Exchr Fd Byp MOV | District Heating Exchanger Feed By-pass Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFA10AA301YB01 | B0NFA10AA301 | YB01 | District Htg Exchr Fd Byp MOV | District Heating Exchanger Feed By-pass Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFA10AA301YB02 | B0NFA10AA301 | YB02 | District Htg Exchr Fd Byp MOV | District Heating Exchanger Feed By-pass Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFA10AA302XB01 | B0NFA10AA302 | XB01 | District Htg Exchr Fd Outl MOV | District Heating Exchanger Feed Outlet Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFA10AA302XB02 | B0NFA10AA302 | XB02 | District Htg Exchr Fd Outl MOV | District Heating Exchanger Feed Outlet Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFA10AA302XB07 | B0NFA10AA302 | XB07 | District Htg Exchr Fd Outl MOV | District Heating Exchanger Feed Outlet Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFA10AA302XB23 | B0NFA10AA302 | XB23 | District Htg Exchr Fd Outl MOV | District Heating Exchanger Feed Outlet Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFA10AA302YB01 | B0NFA10AA302 | YB01 | District Htg Exchr Fd Outl MOV | District Heating Exchanger Feed Outlet Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFA10AA302YB02 | B0NFA10AA302 | YB02 | District Htg Exchr Fd Outl MOV | District Heating Exchanger Feed Outlet Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFA10CF001XQ01 | B0NFA10CF001 | XQ01 | District Htg Exchr Fd Outl Flow | District Heating Exchanger Feed Outlet Flow | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFA10CP001XQ01 | B0NFA10CP001 | XQ01 | District Htg Exchr Fd Outl Press | District Heating Exchanger Feed Outlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFA10CT001AXQ01 | B0NFA10CT001A | XQ01 | District Htg Exchr Fd Outl Temp 1 | District Heating Exchanger Feed Outlet Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFA10CT001BXQ01 | B0NFA10CT001B | XQ01 | District Htg Exchr Fd Outl Temp 2 | District Heating Exchanger Feed Outlet Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFB10AA301XB01 | B0NFB10AA301 | XB01 | District Htg Exchr Fd Inl MOV | District Heating Exchanger Feed Inlet Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFB10AA301XB02 | B0NFB10AA301 | XB02 | District Htg Exchr Fd Inl MOV | District Heating Exchanger Feed Inlet Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFB10AA301XB07 | B0NFB10AA301 | XB07 | District Htg Exchr Fd Inl MOV | District Heating Exchanger Feed Inlet Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFB10AA301XB23 | B0NFB10AA301 | XB23 | District Htg Exchr Fd Inl MOV | District Heating Exchanger Feed Inlet Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFB10AA301YB01 | B0NFB10AA301 | YB01 | District Htg Exchr Fd Inl MOV | District Heating Exchanger Feed Inlet Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFB10AA301YB02 | B0NFB10AA301 | YB02 | District Htg Exchr Fd Inl MOV | District Heating Exchanger Feed Inlet Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFB10CP001XQ01 | B0NFB10CP001 | XQ01 | District Htg Exchr Fd Inl Press | District Heating Exchanger Feed Inlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFB10CT001AXQ01 | B0NFB10CT001A | XQ01 | District Htg Exchr Fd Inl Temp 1 | District Heating Exchanger Feed Inlet Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0NFB10CT001BXQ01 | B0NFB10CT001B | XQ01 | District Htg Exchr Fd Inl Temp 2 | District Heating Exchanger Feed Inlet Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000009 - District Heating | NPE7-EAI-41XX-XXX-PP-XA-008003 | NPE7-EAI-41XX-XXX-PP-XA-008005 | NPE7-EAI-41XX-XXX-IM-XA-008004 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGA10CP001AXQ01 | B0PGA10CP001A | XQ01 | CCW Pmps Com Hdr Disch Press 1 | Closed Cooling Water Pumps Common Header Discharge Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGA10CP001BXQ01 | B0PGA10CP001B | XQ01 | CCW Pmps Com Hdr Disch Press 2 | Closed Cooling Water Pumps Common Header Discharge Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGA13CP001XQ01 | B0PGA13CP001 | XQ01 | CCW Expansion Tank Press | Closed Cooling Water Expansion Tank Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGB10CT001XQ01 | B0PGB10CT001 | XQ01 | Fin Fan Coolers Inlet Temp | Fin Fan Coolers Inlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGB13CP002AXQ01 | B0PGB13CP002A | XQ01 | CCW Pmps Com Hdr Inlet Press 1 | Closed Cooling Water Pumps Common Header Inlet Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGB13CP002BXQ01 | B0PGB13CP002B | XQ01 | CCW Pmps Com Hdr Inlet Press 2 | Closed Cooling Water Pumps Common Header Inlet Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGB13CT001AXQ01 | B0PGB13CT001A | XQ01 | Fin Fan Coolers Outl Temp 1 | Fin Fan Coolers Outlet Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGB13CT001BXQ01 | B0PGB13CT001B | XQ01 | Fin Fan Coolers Outl Temp 2 | Fin Fan Coolers Outlet Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGB25CT001XQ01 | B0PGB25CT001 | XQ01 | Smplg Skid to Hot Wtr Rtn Temp | Sampling Skid to Hot Water Return Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGB31CT001XQ01 | B0PGB31CT001 | XQ01 | Air Compr1 to Hot Wtr Rtn Temp | Air Compressor 1 to Hot Water Return Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGB32CT001XQ01 | B0PGB32CT001 | XQ01 | Air Compr2 to Hot Wtr Rtn Temp | Air Compressor 2 to Hot Water Return Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGB33CT001XQ01 | B0PGB33CT001 | XQ01 | Air Compr3 to Hot Wtr Rtn Temp | Air Compressor 3 to Hot Water Return Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGB41CT001XQ01 | B0PGB41CT001 | XQ01 | HP FwP1 to Hot Wtr Rtn Temp | HP Feedwater P1 to Hot Water Return Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGB42CT001XQ01 | B0PGB42CT001 | XQ01 | HP FwP2 to Hot Wtr Rtn Temp | HP Feedwater P2 to Hot Water Return Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGB43CT001XQ01 | B0PGB43CT001 | XQ01 | HP FwP3 to Hot Wtr Rtn Temp | HP Feedwater P3 to Hot Water Return Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGB51CT001XQ01 | B0PGB51CT001 | XQ01 | CP1 to Hot Wtr Rtn Temp | Condensate Pump 1 to Hot Water Return Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGB52CT001XQ01 | B0PGB52CT001 | XQ01 | CP2 to Hot Wtr Rtn Temp | Condensate Pump 2 to Hot Water Return Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGB61CT001XQ01 | B0PGB61CT001 | XQ01 | Gen Cool1 to Hot Wtr Rtn Temp | Generator Cooling 1 to Hot Water Return Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGB62CT001XQ01 | B0PGB62CT001 | XQ01 | Gen Cool2 to Hot Wtr Rtn Temp | Generator Cooling 2 to Hot Water Return Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGB63CT001XQ01 | B0PGB63CT001 | XQ01 | Gen Cool3 to Hot Wtr Rtn Temp | Generator Cooling 3 to Hot Water Return Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGB64CT001XQ01 | B0PGB64CT001 | XQ01 | Gen Cool4 to Hot Wtr Rtn Temp | Generator Cooling 4 to Hot Water Return Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGB70CT001XQ01 | B0PGB70CT001 | XQ01 | LubO Cool Hdr to Hot Wtr Rtn Temp | Lube Oil Cooling Header to Hot Water Return Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGB80CT001XQ01 | B0PGB80CT001 | XQ01 | Main Xfmr to Hot Wtr Rtn Temp | Main Transformer to Hot Water Return Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGC11CP001XQ01 | B0PGC11CP001 | XQ01 | CCW Pmp1 Suct Fltr DP | Closed Cooling Water Pump 1 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0PGC12CP001XQ01 | B0PGC12CP001 | XQ01 | CCW Pmp2 Suct Fltr DP | Closed Cooling Water Pump 2 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Chemical Dosing Supplier | B0QCB10GH001XB31 | B0QCB10GH001 | XB31 | Corrosion Inhibitor Skid Interface | Corrosion Inhibitor Skid Interface | No General Alarm | General Alarm |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000017 - Chemical Dosing | NPE7-EAI-41XX-XXX-PP-XA-007617 | NPE7-EAI-41XX-XXX-PP-XA-007634 | NPE7-EAI-41XX-XXX-IM-XA-007615 | Chemical Dosing System | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Chemical Dosing Supplier | B0QCB10GH001XB33 | B0QCB10GH001 | XB33 | Corrosion Inhibitor Skid Interface | Corrosion Inhibitor Skid Interface | PLC n fail | PLC fail |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000017 - Chemical Dosing | NPE7-EAI-41XX-XXX-PP-XA-007617 | NPE7-EAI-41XX-XXX-PP-XA-007634 | NPE7-EAI-41XX-XXX-IM-XA-007615 | Chemical Dosing System | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Chemical Dosing Supplier | B0QCD10GH001XB31 | B0QCD10GH001 | XB31 | Ammonia Skid Interface | Ammonia Skid Interface | No General Alarm | General Alarm |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000017 - Chemical Dosing | NPE7-EAI-41XX-XXX-PP-XA-007617 | NPE7-EAI-41XX-XXX-PP-XA-007634 | NPE7-EAI-41XX-XXX-IM-XA-007615 | Chemical Dosing System | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Chemical Dosing Supplier | B0QCD10GH001XB33 | B0QCD10GH001 | XB33 | Ammonia Skid Interface | Ammonia Skid Interface | PLC n fail | PLC fail |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000017 - Chemical Dosing | NPE7-EAI-41XX-XXX-PP-XA-007617 | NPE7-EAI-41XX-XXX-PP-XA-007634 | NPE7-EAI-41XX-XXX-IM-XA-007615 | Chemical Dosing System | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Chemical Dosing Supplier | B0QCF10GH001XB31 | B0QCF10GH001 | XB31 | Sodium Hypochlorite Skid Interface | Sodium Hypochlorite Skid Interface | No General Alarm | General Alarm |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000017 - Chemical Dosing | NPE7-EAI-41XX-XXX-PP-XA-007617 | NPE7-EAI-41XX-XXX-PP-XA-007634 | NPE7-EAI-41XX-XXX-IM-XA-007615 | Chemical Dosing System | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Chemical Dosing Supplier | B0QCF10GH001XB33 | B0QCF10GH001 | XB33 | Sodium Hypochlorite Skid Interface | Sodium Hypochlorite Skid Interface | PLC n fail | PLC fail |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000017 - Chemical Dosing | NPE7-EAI-41XX-XXX-PP-XA-007617 | NPE7-EAI-41XX-XXX-PP-XA-007634 | NPE7-EAI-41XX-XXX-IM-XA-007615 | Chemical Dosing System | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Chemical Dosing Supplier | B0QCL10GH001XB31 | B0QCL10GH001 | XB31 | Propilenglycol Skid Interface | Propilenglycol Skid Interface | No General Alarm | General Alarm |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000017 - Chemical Dosing | NPE7-EAI-41XX-XXX-PP-XA-007617 | NPE7-EAI-41XX-XXX-PP-XA-007634 | NPE7-EAI-41XX-XXX-IM-XA-007615 | Chemical Dosing System | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Chemical Dosing Supplier | B0QCL10GH001XB33 | B0QCL10GH001 | XB33 | Propilenglycol Skid Interface | Propilenglycol Skid Interface | PLC n fail | PLC fail |  |  | DI | 24VDC | S |  |  | B0CRM01GH003 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000017 - Chemical Dosing | NPE7-EAI-41XX-XXX-PP-XA-007617 | NPE7-EAI-41XX-XXX-PP-XA-007634 | NPE7-EAI-41XX-XXX-IM-XA-007615 | Chemical Dosing System | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0QEA10CP001XQ01 | B0QEA10CP001 | XQ01 | Wet Air Buffer Tank Press | Wet Air Buffer Tank Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA11AH001XB01 | B0QEA11AH001 | XB01 | Adsorption Air Dryer 1 | Adsorption Air Dryer 1 | Running |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA11AH001XB22 | B0QEA11AH001 | XB22 | Adsorption Air Dryer 1 | Adsorption Air Dryer 1 | Remote |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA11AH001XN01 | B0QEA11AH001 | XN01 | Adsorption Air Dryer 1 | Adsorption Air Dryer 1 | n General Warning |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA11AH001YB01 | B0QEA11AH001 | YB01 | Adsorption Air Dryer 1 | Adsorption Air Dryer 1 | Start Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA11AH001YB02 | B0QEA11AH001 | YB02 | Adsorption Air Dryer 1 | Adsorption Air Dryer 1 | Stop Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA11AN001XB01 | B0QEA11AN001 | XB01 | Air Compressor 1 | Air Compressor 1 | Running |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA11AN001XB22 | B0QEA11AN001 | XB22 | Air Compressor 1 | Air Compressor 1 | Remote |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA11AN001XN01 | B0QEA11AN001 | XN01 | Air Compressor 1 | Air Compressor 1 | n General Warning |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA11AN001YB01 | B0QEA11AN001 | YB01 | Air Compressor 1 | Air Compressor 1 | Start Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA11AN001YB02 | B0QEA11AN001 | YB02 | Air Compressor 1 | Air Compressor 1 | Stop Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA11CP001XQ01 | B0QEA11CP001 | XQ01 | Compress Air Prefilter 1 | Compressed Air Prefilter 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA11CP002XQ01 | B0QEA11CP002 | XQ01 | Compress Air Postfilter 1 | Compressed Air Postfilter 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA12AH001XB01 | B0QEA12AH001 | XB01 | Adsorption Air Dryer 2 | Adsorption Air Dryer 2 | Running |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA12AH001XB22 | B0QEA12AH001 | XB22 | Adsorption Air Dryer 2 | Adsorption Air Dryer 2 | Remote |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA12AH001XN01 | B0QEA12AH001 | XN01 | Adsorption Air Dryer 2 | Adsorption Air Dryer 2 | n General Warning |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA12AH001YB01 | B0QEA12AH001 | YB01 | Adsorption Air Dryer 2 | Adsorption Air Dryer 2 | Start Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA12AH001YB02 | B0QEA12AH001 | YB02 | Adsorption Air Dryer 2 | Adsorption Air Dryer 2 | Stop Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA12AN001XB01 | B0QEA12AN001 | XB01 | Air Compressor 2 | Air Compressor 2 | Running |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA12AN001XB22 | B0QEA12AN001 | XB22 | Air Compressor 2 | Air Compressor 2 | Remote |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA12AN001XN01 | B0QEA12AN001 | XN01 | Air Compressor 2 | Air Compressor 2 | n General Warning |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA12AN001YB01 | B0QEA12AN001 | YB01 | Air Compressor 2 | Air Compressor 2 | Start Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA12AN001YB02 | B0QEA12AN001 | YB02 | Air Compressor 2 | Air Compressor 2 | Stop Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA12CP001XQ01 | B0QEA12CP001 | XQ01 | Compress Air Prefilter 2 | Compressed Air Prefilter 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA12CP002XQ01 | B0QEA12CP002 | XQ01 | Compress Air Postfilter 2 | Compressed Air Postfilter 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA13AN001XB01 | B0QEA13AN001 | XB01 | Air Compressor 3 | Air Compressor 3 | Running |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA13AN001XB22 | B0QEA13AN001 | XB22 | Air Compressor 3 | Air Compressor 3 | Remote |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA13AN001XN01 | B0QEA13AN001 | XN01 | Air Compressor 3 | Air Compressor 3 | n General Warning |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA13AN001YB01 | B0QEA13AN001 | YB01 | Air Compressor 3 | Air Compressor 3 | Start Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
AIR Compressor Supplier | B0QEA13AN001YB02 | B0QEA13AN001 | YB02 | Air Compressor 3 | Air Compressor 3 | Stop Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 | Compressed Air Generation | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0QEA20CP001XQ01 | B0QEA20CP001 | XQ01 | Svce Air Rcvr Tank Press | Service Air Control Valve Tank Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0QEB10CP001XQ01 | B0QEB10CP001 | XQ01 | Svce Air Rcvr Outl Press | Service Air Control Valve Outlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0QEB10CP002XQ01 | B0QEB10CP002 | XQ01 | Svce Air Distr Hdr Press | Service Air District Header Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0QFA10CP001XQ01 | B0QFA10CP001 | XQ01 | Instr Air Rcvr Tank Press | Instrument Air Control Valver Tank Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0QFB10CP001XQ01 | B0QFB10CP001 | XQ01 | Instr Air Distr Hdr Press | Instrument Air District Header Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B0QFB15CP001XQ01 | B0QFB15CP001 | XQ01 | Instr Air Distr Ring Press | Instrument Air District Ring Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AX-XXX-PD-XA-000003 - Compressed Air | NPE7-EAI-41AX-XXX-PP-XA-007618 | NPE7-EAI-41AX-XXX-PP-XA-007636 | NPE7-EAI-41AX-XXX-IM-XA-007619 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B0QUA80CQ001XQ01 | B0QUA80CQ001 | XQ01 | FW Pmps Suct DO | Feedwater Pumps Suction Digital Output | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B0QUA80CQ002XQ01 | B0QUA80CQ002 | XQ01 | FW Pmps Suct PH | Feedwater Pumps Suction PH | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B0QUA80CQ003XQ01 | B0QUA80CQ003 | XQ01 | FW Pmps Suct DC | Feedwater Pumps Suction DC | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B0QUA80CQ004XQ01 | B0QUA80CQ004 | XQ01 | FW Pmps Suct AC | Feedwater Pumps Suction AC | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B0QUB90CQ001XQ01 | B0QUB90CQ001 | XQ01 | Demi Wtr Press Grp DC | Demi Water Pressure Group DC | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B0QUB90CQ002XQ01 | B0QUB90CQ002 | XQ01 | Demi Wtr Press Grp SIO2 | Demi Water Pressure Group SIO2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B0QUC20CQ001XQ01 | B0QUC20CQ001 | XQ01 | Conds Dnstrm LP Prehtr PH | Condensate Downstream LP Preheater PH | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B0QUC20CQ002XQ01 | B0QUC20CQ002 | XQ01 | Conds Dnstrm LP Prehtr DC | Condensate Downstream LP Preheater DC | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B0QUC20CQ003XQ01 | B0QUC20CQ003 | XQ01 | Conds Dnstrm LP Prehtr AC | Condensate Downstream LP Preheater AC | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B0QUC20CQ004XQ01 | B0QUC20CQ004 | XQ01 | Conds Dnstrm LP Prehtr DCC | Condensate Downstream LP Preheater DCC | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Firefighting Supplier | B0SGY10EA001XB31 | B0SGY10GH001 | XB31 | Fire Fighting System PLC | Fire Fighting System PLC | PLC n fail |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | - | NPE7-EAI-41XX-XXX-PP-XA-007842 | NPE7-EAI-41XX-XXX-PP-XA-007638 | NPE7-EAI-41AC-XXX-IM-XA-007646 | Fire Detection & Alarm Systems | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Firefighting Supplier | B0SGY10EA001XB56 | B0SGY10GH001 | XB56 | Fire Fighting System No General | Fire Fighting System No General | No General Gas Alarm |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | - | NPE7-EAI-41XX-XXX-PP-XA-007842 | NPE7-EAI-41XX-XXX-PP-XA-007638 | NPE7-EAI-41AC-XXX-IM-XA-007646 | Fire Detection & Alarm Systems | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Firefighting Supplier | B0SGY10EA001XB66 | B0SGY10GH001 | XB66 | Fire Fighting System No General | Fire Fighting System No General | No General Fire Alarm |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | - | NPE7-EAI-41XX-XXX-PP-XA-007842 | NPE7-EAI-41XX-XXX-PP-XA-007638 | NPE7-EAI-41AC-XXX-IM-XA-007646 | Fire Detection & Alarm Systems | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1EKG01AA001XB01 | B1EKG01AA001 | XB01 | Natural Gas Line 1 IV | Natural Gas Line 1 Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000011 - Natural Gas | NPE7-EAI-41XX-XXX-PP-XA-007643 | NPE7-EAI-41XX-XXX-PP-XA-007646 | NPE7-EAI-41XX-XXX-IM-XA-007643 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1EKG01AA001XB02 | B1EKG01AA001 | XB02 | Natural Gas Line 1 IV | Natural Gas Line 1 Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000011 - Natural Gas | NPE7-EAI-41XX-XXX-PP-XA-007643 | NPE7-EAI-41XX-XXX-PP-XA-007646 | NPE7-EAI-41XX-XXX-IM-XA-007643 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1GHE10CL001AXQ01 | B1GHE10CL001A | XQ01 | B1: Proc Wtr Tnk Blr Lvl 1 | B1: Process Water Tank Boiler Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1GHE10CL001BXQ01 | B1GHE10CL001B | XQ01 | B1: Proc Wtr Tnk Blr Lvl 2 | B1: Process Water Tank Boiler Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1GHE11CP001XQ01 | B1GHE11CP001 | XQ01 | B1: Proc Wtr Pmp1 Suct Fltr DP | B1: Process Water Pump 1 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1GHE12CP001XQ01 | B1GHE12CP001 | XQ01 | B1: Proc Wtr Pmp2 Suct Fltr DP | B1: Process Water Pump 2 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1GHE20CP001XQ01 | B1GHE20CP001 | XQ01 | B1: Proc Wtr Pmps Disch Press | B1: Process Water Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1HAD50AA301XB01 | B1HAD50AA301 | XB01 | B1: Blr to FluGas HtExchg Stm MOV | B1: Boiler to Flue Gas Heat Exchanger Steam Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1HAD50AA301XB02 | B1HAD50AA301 | XB02 | B1: Blr to FluGas HtExchg Stm MOV | B1: Boiler to Flue Gas Heat Exchanger Steam Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1HAD50AA301XB07 | B1HAD50AA301 | XB07 | B1: Blr to FluGas HtExchg Stm MOV | B1: Boiler to Flue Gas Heat Exchanger Steam Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1HAD50AA301XB23 | B1HAD50AA301 | XB23 | B1: Blr to FluGas HtExchg Stm MOV | B1: Boiler to Flue Gas Heat Exchanger Steam Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1HAD50AA301YB01 | B1HAD50AA301 | YB01 | B1: Blr to FluGas HtExchg Stm MOV | B1: Boiler to Flue Gas Heat Exchanger Steam Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1HAD50AA301YB02 | B1HAD50AA301 | YB02 | B1: Blr to FluGas HtExchg Stm MOV | B1: Boiler to Flue Gas Heat Exchanger Steam Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1HAD50AA302XB01 | B1HAD50AA302 | XB01 | B1: BlrDrm Pot B1HAD50 Drn Vlv | B1: Boiler Drum Pot B1HAD50 Drain Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1HAD50AA302XB02 | B1HAD50AA302 | XB02 | B1: BlrDrm Pot B1HAD50 Drn Vlv | B1: Boiler Drum Pot B1HAD50 Drain Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1HAD50AA302YB01 | B1HAD50AA302 | YB01 | B1: BlrDrm Pot B1HAD50 Drn Vlv | B1: Boiler Drum Pot B1HAD50 Drain Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1HAD50AA401XQ13 | B1HAD50AA401 | XQ13 | B1: Blr to FluGas HtExchg Stm CV | B1: Boiler to Flue Gas Heat Exchanger Steam Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1HAD50AA401YQ01 | B1HAD50AA401 | YQ01 | B1: Blr to FluGas HtExchg Stm CV | B1: Boiler to Flue Gas Heat Exchanger Steam Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1HAD50CL001XG01 | B1HAD50CL001 | XG01 | B1: BlrDrm Pot B1HAD50 Lvl Sw | B1: Boiler Drum Pot B1HAD50 Level Switch | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | LS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1HAD50CL002XG01 | B1HAD50CL002 | XG01 | B1: BlrDrm Pot B1HAD50 Lvl Sw | B1: Boiler Drum Pot B1HAD50 Level Switch | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | LS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1HAD50CP001XQ01 | B1HAD50CP001 | XQ01 | B1: Blr to FluGas HtExchg Stm Press | B1: Boiler to Flue Gas Heat Exchanger Steam Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1HAD50CT001XQ01 | B1HAD50CT001 | XQ01 | B1: Blr to FluGas HtExchg Stm Temp | B1: Boiler to Flue Gas Heat Exchanger Steam Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CEMS Supplier | B1HNE10CP001XQ01 | B1HNE10CP001 | XQ01 | B1: CEMS Stack Press Abs | B1: CEMS Stack Pressure Absolute | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41CX-XXX-PD-XA-000016 - Stack/CEMS | NPE7-EAI-41XX-XXX-PP-XA-007619 | NPE7-EAI-41XX-XXX-PP-XA-007639 | NPE7-EAI-41XX-XXX-IM-XA-007617 | CEMS | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CEMS Supplier | B1HNE10CT001XQ01 | B1HNE10CT001 | XQ01 | B1: CEMS Stack Temp | B1: CEMS Stack Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41CX-XXX-PD-XA-000016 - Stack/CEMS | NPE7-EAI-41XX-XXX-PP-XA-007619 | NPE7-EAI-41XX-XXX-PP-XA-007639 | NPE7-EAI-41XX-XXX-IM-XA-007617 | CEMS | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CEMS Supplier | B1HNE10GH001XB01 | B1HNE10GH001 | XB01 | B1: CEMS Interface | B1: CEMS Interface | in Operation |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41CX-XXX-PD-XA-000016 - Stack/CEMS | NPE7-EAI-41XX-XXX-PP-XA-007619 | NPE7-EAI-41XX-XXX-PP-XA-007639 | NPE7-EAI-41XX-XXX-IM-XA-007617 | CEMS | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CEMS Supplier | B1HNE10GH001XB04 | B1HNE10GH001 | XB04 | B1: CEMS Interface | B1: CEMS Interface | In Calib/Mainten Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41CX-XXX-PD-XA-000016 - Stack/CEMS | NPE7-EAI-41XX-XXX-PP-XA-007619 | NPE7-EAI-41XX-XXX-PP-XA-007639 | NPE7-EAI-41XX-XXX-IM-XA-007617 | CEMS | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CEMS Supplier | B1HNE10GH001XB31 | B1HNE10GH001 | XB31 | B1: CEMS Interface | B1: CEMS Interface | No General Alarm | General Alarm |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41CX-XXX-PD-XA-000016 - Stack/CEMS | NPE7-EAI-41XX-XXX-PP-XA-007619 | NPE7-EAI-41XX-XXX-PP-XA-007639 | NPE7-EAI-41XX-XXX-IM-XA-007617 | CEMS | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CEMS Supplier | B1HNE10GH001XB33 | B1HNE10GH001 | XB33 | B1: CEMS Interface | B1: CEMS Interface | No Emission Limit Alarm | Emission Limit Alarm |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41CX-XXX-PD-XA-000016 - Stack/CEMS | NPE7-EAI-41XX-XXX-PP-XA-007619 | NPE7-EAI-41XX-XXX-PP-XA-007639 | NPE7-EAI-41XX-XXX-IM-XA-007617 | CEMS | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LAC40CP001XQ01 | B1LAC40CP001 | XQ01 | B1: FW Pmps to Blr Press | B1: Feedwater Pumps to Boiler Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LAC40CT001XQ01 | B1LAC40CT001 | XQ01 | B1: FW Pmps to Blr Temp | B1: Feedwater Pumps to Boiler Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LAF31AA301XB01 | B1LAF31AA301 | XB01 | B1: Bypass CV Attemp Water IV | B1: Bypass Control Valve Attemperation Water Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LAF31AA301XB02 | B1LAF31AA301 | XB02 | B1: Bypass CV Attemp Water IV | B1: Bypass Control Valve Attemperation Water Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LAF31AA301YB01 | B1LAF31AA301 | YB01 | B1: Bypass CV Attemp Water IV | B1: Bypass Control Valve Attemperation Water Isolation Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LAF31AA401XQ13 | B1LAF31AA401 | XQ13 | B1: Main Steam Bypass Attemp CV | B1: Main Steam Bypass Attemperation Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LAF31AA401YQ01 | B1LAF31AA401 | YQ01 | B1: Main Steam Bypass Attemp CV | B1: Main Steam Bypass Attemperation Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LAF31CF001AXQ01 | B1LAF31CF001A | XQ01 | B1: MS Bypass Attemp Flow 1 | B1: Main Steam Bypass Attemperation Flow 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LAF31CF001BXQ01 | B1LAF31CF001B | XQ01 | B1: MS Bypass Attemp Flow 2 | B1: Main Steam Bypass Attemperation Flow 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LAF31CP001XQ01 | B1LAF31CP001 | XQ01 | B1: MS Byp Attemp CV Inl Press | B1: Main Steam By-pass Attemperation Control Valve Inlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LAF31CP002XQ01 | B1LAF31CP002 | XQ01 | B1: MS Byp Attemp CV Outl Press | B1: Main Steam By-pass Attemperation Control Valve Outlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LAF31CP003XQ01 | B1LAF31CP003 | XQ01 | B1: MS Byp Attemp Fltr DP | B1: Main Steam By-pass Attemperation Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA10AA301XB01 | B1LBA10AA301 | XB01 | B1: MS Isol MOV | B1: Main Steam Isolation Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA10AA301XB02 | B1LBA10AA301 | XB02 | B1: MS Isol MOV | B1: Main Steam Isolation Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA10AA301XB07 | B1LBA10AA301 | XB07 | B1: MS Isol MOV | B1: Main Steam Isolation Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA10AA301XB23 | B1LBA10AA301 | XB23 | B1: MS Isol MOV | B1: Main Steam Isolation Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA10AA301YB01 | B1LBA10AA301 | YB01 | B1: MS Isol MOV | B1: Main Steam Isolation Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA10AA301YB02 | B1LBA10AA301 | YB02 | B1: MS Isol MOV | B1: Main Steam Isolation Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA10AA302XB01 | B1LBA10AA302 | XB01 | B1: MS Pot B1LBA10 Drn MOV | B1: Main Steam Pot B1LBA10 Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA10AA302XB02 | B1LBA10AA302 | XB02 | B1: MS Pot B1LBA10 Drn MOV | B1: Main Steam Pot B1LBA10 Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA10AA302XB07 | B1LBA10AA302 | XB07 | B1: MS Pot B1LBA10 Drn MOV | B1: Main Steam Pot B1LBA10 Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA10AA302XB23 | B1LBA10AA302 | XB23 | B1: MS Pot B1LBA10 Drn MOV | B1: Main Steam Pot B1LBA10 Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA10AA302XQ13 | B1LBA10AA302 | XQ13 | B1: MS Pot B1LBA10 Drn MOV | B1: Main Steam Pot B1LBA10 Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA10AA302YB01 | B1LBA10AA302 | YB01 | B1: MS Pot B1LBA10 Drn MOV | B1: Main Steam Pot B1LBA10 Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA10AA302YB02 | B1LBA10AA302 | YB02 | B1: MS Pot B1LBA10 Drn MOV | B1: Main Steam Pot B1LBA10 Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA10CP001AXQ01 | B1LBA10CP001A | XQ01 | B1: MS from Boiler Press 1 | B1: Main Steam from Boiler Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA10CP001BXQ01 | B1LBA10CP001B | XQ01 | B1: MS from Boiler Press 2 | B1: Main Steam from Boiler Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA10CT001AXQ01 | B1LBA10CT001A | XQ01 | B1: MS from Boiler Temp 1 | B1: Main Steam from Boiler Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA10CT001BXQ01 | B1LBA10CT001B | XQ01 | B1: MS from Boiler Temp 2 | B1: Main Steam from Boiler Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA10CT001CXQ01 | B1LBA10CT001C | XQ01 | B1: MS from Boiler Temp 3 | B1: Main Steam from Boiler Temperature 3 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | C | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA10CT001XQ01 | B1LBA10CT001 | XQ01 | B1: MS Pot B1LBA10 Temp | B1: Main Steam Pot B1LBA10 Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA20AA301XB01 | B1LBA20AA301 | XB01 | B1: MS Pot Bfr Bypass Drn MOV | B1: Main Steam Pot Before Bypass Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA20AA301XB02 | B1LBA20AA301 | XB02 | B1: MS Pot Bfr Bypass Drn MOV | B1: Main Steam Pot Before Bypass Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA20AA301XB07 | B1LBA20AA301 | XB07 | B1: MS Pot Bfr Bypass Drn MOV | B1: Main Steam Pot Before Bypass Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA20AA301XB23 | B1LBA20AA301 | XB23 | B1: MS Pot Bfr Bypass Drn MOV | B1: Main Steam Pot Before Bypass Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA20AA301XQ13 | B1LBA20AA301 | XQ13 | B1: MS Pot Bfr Bypass Drn MOV | B1: Main Steam Pot Before Bypass Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA20AA301YB01 | B1LBA20AA301 | YB01 | B1: MS Pot Bfr Bypass Drn MOV | B1: Main Steam Pot Before Bypass Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA20AA301YB02 | B1LBA20AA301 | YB02 | B1: MS Pot Bfr Bypass Drn MOV | B1: Main Steam Pot Before Bypass Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBA20CT001XQ01 | B1LBA20CT001 | XQ01 | B1: MS Pot Bfr Bypass Temp | B1: Main Steam Pot Before Bypass Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30AA301XB01 | B1LBG30AA301 | XB01 | B1: AuxStm to AirPrehtr Byp MOV | B1: Aux Steam to Air Preheater By-pass Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30AA301XB02 | B1LBG30AA301 | XB02 | B1: AuxStm to AirPrehtr Byp MOV | B1: Aux Steam to Air Preheater By-pass Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30AA301XB07 | B1LBG30AA301 | XB07 | B1: AuxStm to AirPrehtr Byp MOV | B1: Aux Steam to Air Preheater By-pass Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30AA301XB23 | B1LBG30AA301 | XB23 | B1: AuxStm to AirPrehtr Byp MOV | B1: Aux Steam to Air Preheater By-pass Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30AA301XQ13 | B1LBG30AA301 | XQ13 | B1: AuxStm to AirPrehtr Byp MOV | B1: Aux Steam to Air Preheater By-pass Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30AA301YB01 | B1LBG30AA301 | YB01 | B1: AuxStm to AirPrehtr Byp MOV | B1: Aux Steam to Air Preheater By-pass Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30AA301YB02 | B1LBG30AA301 | YB02 | B1: AuxStm to AirPrehtr Byp MOV | B1: Aux Steam to Air Preheater By-pass Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30AA302XB01 | B1LBG30AA302 | XB01 | B1: AuxStm to AirPrehtr Pot Drn MOV | B1: Aux Steam to Air Preheater Pot Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30AA302XB02 | B1LBG30AA302 | XB02 | B1: AuxStm to AirPrehtr Pot Drn MOV | B1: Aux Steam to Air Preheater Pot Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30AA302XB07 | B1LBG30AA302 | XB07 | B1: AuxStm to AirPrehtr Pot Drn MOV | B1: Aux Steam to Air Preheater Pot Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30AA302XB23 | B1LBG30AA302 | XB23 | B1: AuxStm to AirPrehtr Pot Drn MOV | B1: Aux Steam to Air Preheater Pot Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30AA302XQ13 | B1LBG30AA302 | XQ13 | B1: AuxStm to AirPrehtr Pot Drn MOV | B1: Aux Steam to Air Preheater Pot Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30AA302YB01 | B1LBG30AA302 | YB01 | B1: AuxStm to AirPrehtr Pot Drn MOV | B1: Aux Steam to Air Preheater Pot Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30AA302YB02 | B1LBG30AA302 | YB02 | B1: AuxStm to AirPrehtr Pot Drn MOV | B1: Aux Steam to Air Preheater Pot Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30AA401XQ13 | B1LBG30AA401 | XQ13 | B1: AuxStm to AirPrehtr CV | B1: Aux Steam to Air Preheater Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30AA401YQ01 | B1LBG30AA401 | YQ01 | B1: AuxStm to AirPrehtr CV | B1: Aux Steam to Air Preheater Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30CF001AXQ01 | B1LBG30CF001A | XQ01 | B1: AuxStm to AirPrehtr Flow 1 | B1: Aux Steam to Air Preheater Flow 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30CF001BXQ01 | B1LBG30CF001B | XQ01 | B1: AuxStm to AirPrehtr Flow 2 | B1: Aux Steam to Air Preheater Flow 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30CP001XQ01 | B1LBG30CP001 | XQ01 | B1: AuxStm to AirPrehtr Press | B1: Aux Steam to Air Preheater Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30CT001AXQ01 | B1LBG30CT001A | XQ01 | B1: AuxStm to AirPrehtr Temp 1 | B1: Aux Steam to Air Preheater Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30CT001BXQ01 | B1LBG30CT001B | XQ01 | B1: AuxStm to AirPrehtr Temp 2 | B1: Aux Steam to Air Preheater Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG30CT002XQ01 | B1LBG30CT002 | XQ01 | B1: AuxStm to AirPrehtr Drn Temp | B1: Aux Steam to Air Preheater Drain Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG31AA301XB01 | B1LBG31AA301 | XB01 | B1: Blr to PriAirPrehtr Byp MOV | B1: Boiler to Primary Air Preheater By-pass Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG31AA301XB02 | B1LBG31AA301 | XB02 | B1: Blr to PriAirPrehtr Byp MOV | B1: Boiler to Primary Air Preheater By-pass Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG31AA301XB07 | B1LBG31AA301 | XB07 | B1: Blr to PriAirPrehtr Byp MOV | B1: Boiler to Primary Air Preheater By-pass Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG31AA301XB23 | B1LBG31AA301 | XB23 | B1: Blr to PriAirPrehtr Byp MOV | B1: Boiler to Primary Air Preheater By-pass Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG31AA301XQ13 | B1LBG31AA301 | XQ13 | B1: Blr to PriAirPrehtr Byp MOV | B1: Boiler to Primary Air Preheater By-pass Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG31AA301YB01 | B1LBG31AA301 | YB01 | B1: Blr to PriAirPrehtr Byp MOV | B1: Boiler to Primary Air Preheater By-pass Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG31AA301YB02 | B1LBG31AA301 | YB02 | B1: Blr to PriAirPrehtr Byp MOV | B1: Boiler to Primary Air Preheater By-pass Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG31AA302XB01 | B1LBG31AA302 | XB01 | B1: PriAirPrehtr to BlwDn Tnk MOV | B1: Primary Air Preheater to Blowdown Tank Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG31AA302XB02 | B1LBG31AA302 | XB02 | B1: PriAirPrehtr to BlwDn Tnk MOV | B1: Primary Air Preheater to Blowdown Tank Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG31AA302XB07 | B1LBG31AA302 | XB07 | B1: PriAirPrehtr to BlwDn Tnk MOV | B1: Primary Air Preheater to Blowdown Tank Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG31AA302XB23 | B1LBG31AA302 | XB23 | B1: PriAirPrehtr to BlwDn Tnk MOV | B1: Primary Air Preheater to Blowdown Tank Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG31AA302XQ13 | B1LBG31AA302 | XQ13 | B1: PriAirPrehtr to BlwDn Tnk MOV | B1: Primary Air Preheater to Blowdown Tank Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG31AA302YB01 | B1LBG31AA302 | YB01 | B1: PriAirPrehtr to BlwDn Tnk MOV | B1: Primary Air Preheater to Blowdown Tank Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG31AA302YB02 | B1LBG31AA302 | YB02 | B1: PriAirPrehtr to BlwDn Tnk MOV | B1: Primary Air Preheater to Blowdown Tank Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG31AA401XQ13 | B1LBG31AA401 | XQ13 | B1: Blr to PriAirPrehtr CV | B1: Boiler to Primary Air Preheater Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG31AA401YQ01 | B1LBG31AA401 | YQ01 | B1: Blr to PriAirPrehtr CV | B1: Boiler to Primary Air Preheater Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG31CP001XQ01 | B1LBG31CP001 | XQ01 | B1: Blr to PriAirPrehtr Byp Press | B1: Boiler to Primary Air Preheater By-pass Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG31CT001XQ01 | B1LBG31CT001 | XQ01 | B1: PriAirPrehtr to BlwDn Tnk Temp | B1: Primary Air Preheater to Blowdown Tank Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG32AA301XB01 | B1LBG32AA301 | XB01 | B1: Blr to SecAirPrehtr Byp MOV | B1: Boiler to Secondary Air Preheater By-pass Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG32AA301XB02 | B1LBG32AA301 | XB02 | B1: Blr to SecAirPrehtr Byp MOV | B1: Boiler to Secondary Air Preheater By-pass Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG32AA301XB07 | B1LBG32AA301 | XB07 | B1: Blr to SecAirPrehtr Byp MOV | B1: Boiler to Secondary Air Preheater By-pass Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG32AA301XB23 | B1LBG32AA301 | XB23 | B1: Blr to SecAirPrehtr Byp MOV | B1: Boiler to Secondary Air Preheater By-pass Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG32AA301XQ13 | B1LBG32AA301 | XQ13 | B1: Blr to SecAirPrehtr Byp MOV | B1: Boiler to Secondary Air Preheater By-pass Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG32AA301YB01 | B1LBG32AA301 | YB01 | B1: Blr to SecAirPrehtr Byp MOV | B1: Boiler to Secondary Air Preheater By-pass Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG32AA301YB02 | B1LBG32AA301 | YB02 | B1: Blr to SecAirPrehtr Byp MOV | B1: Boiler to Secondary Air Preheater By-pass Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG32AA302XB01 | B1LBG32AA302 | XB01 | B1: SecAirPrehtr to BlwDn Tnk MOV | B1: Secondary Air Preheater to Blowdown Tank Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG32AA302XB02 | B1LBG32AA302 | XB02 | B1: SecAirPrehtr to BlwDn Tnk MOV | B1: Secondary Air Preheater to Blowdown Tank Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG32AA302XB07 | B1LBG32AA302 | XB07 | B1: SecAirPrehtr to BlwDn Tnk MOV | B1: Secondary Air Preheater to Blowdown Tank Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG32AA302XB23 | B1LBG32AA302 | XB23 | B1: SecAirPrehtr to BlwDn Tnk MOV | B1: Secondary Air Preheater to Blowdown Tank Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG32AA302XQ13 | B1LBG32AA302 | XQ13 | B1: SecAirPrehtr to BlwDn Tnk MOV | B1: Secondary Air Preheater to Blowdown Tank Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG32AA302YB01 | B1LBG32AA302 | YB01 | B1: SecAirPrehtr to BlwDn Tnk MOV | B1: Secondary Air Preheater to Blowdown Tank Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG32AA302YB02 | B1LBG32AA302 | YB02 | B1: SecAirPrehtr to BlwDn Tnk MOV | B1: Secondary Air Preheater to Blowdown Tank Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG32AA401XQ13 | B1LBG32AA401 | XQ13 | B1: Blr to SecAirPrehtr CV | B1: Boiler to Secondary Air Preheater Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG32AA401YQ01 | B1LBG32AA401 | YQ01 | B1: Blr to SecAirPrehtr CV | B1: Boiler to Secondary Air Preheater Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG32CP001XQ01 | B1LBG32CP001 | XQ01 | B1: Blr to SecAirPrehtr Byp Press | B1: Boiler to Secondary Air Preheater By-pass Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG32CT001XQ01 | B1LBG32CT001 | XQ01 | B1: SecAirPrehtr to BlwDn Tnk Temp | B1: Secondary Air Preheater to Blowdown Tank Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA301XB01 | B1LBG33AA301 | XB01 | B1: Sealing Air Prehtr MOV | B1: Sealing Air Preheater Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA301XB02 | B1LBG33AA301 | XB02 | B1: Sealing Air Prehtr MOV | B1: Sealing Air Preheater Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA301XB07 | B1LBG33AA301 | XB07 | B1: Sealing Air Prehtr MOV | B1: Sealing Air Preheater Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA301XB23 | B1LBG33AA301 | XB23 | B1: Sealing Air Prehtr MOV | B1: Sealing Air Preheater Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA301YB01 | B1LBG33AA301 | YB01 | B1: Sealing Air Prehtr MOV | B1: Sealing Air Preheater Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA301YB02 | B1LBG33AA301 | YB02 | B1: Sealing Air Prehtr MOV | B1: Sealing Air Preheater Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA302XB01 | B1LBG33AA302 | XB01 | B1: Sealing Air Prehtr Byp MOV | B1: Sealing Air Preheater By-pass Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA302XB02 | B1LBG33AA302 | XB02 | B1: Sealing Air Prehtr Byp MOV | B1: Sealing Air Preheater By-pass Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA302XB07 | B1LBG33AA302 | XB07 | B1: Sealing Air Prehtr Byp MOV | B1: Sealing Air Preheater By-pass Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA302XB23 | B1LBG33AA302 | XB23 | B1: Sealing Air Prehtr Byp MOV | B1: Sealing Air Preheater By-pass Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA302XQ13 | B1LBG33AA302 | XQ13 | B1: Sealing Air Prehtr Byp MOV | B1: Sealing Air Preheater By-pass Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA302YB01 | B1LBG33AA302 | YB01 | B1: Sealing Air Prehtr Byp MOV | B1: Sealing Air Preheater By-pass Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA302YB02 | B1LBG33AA302 | YB02 | B1: Sealing Air Prehtr Byp MOV | B1: Sealing Air Preheater By-pass Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA303XB01 | B1LBG33AA303 | XB01 | B1: Sealing AirPrehtr Pot Drn MOV | B1: Sealing Air Preheater Pot Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA303XB02 | B1LBG33AA303 | XB02 | B1: Sealing AirPrehtr Pot Drn MOV | B1: Sealing Air Preheater Pot Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA303XB07 | B1LBG33AA303 | XB07 | B1: Sealing AirPrehtr Pot Drn MOV | B1: Sealing Air Preheater Pot Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA303XB23 | B1LBG33AA303 | XB23 | B1: Sealing AirPrehtr Pot Drn MOV | B1: Sealing Air Preheater Pot Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA303XQ13 | B1LBG33AA303 | XQ13 | B1: Sealing AirPrehtr Pot Drn MOV | B1: Sealing Air Preheater Pot Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA303YB01 | B1LBG33AA303 | YB01 | B1: Sealing AirPrehtr Pot Drn MOV | B1: Sealing Air Preheater Pot Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA303YB02 | B1LBG33AA303 | YB02 | B1: Sealing AirPrehtr Pot Drn MOV | B1: Sealing Air Preheater Pot Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA401XQ13 | B1LBG33AA401 | XQ13 | B1: Sealing Air Prehtr CV | B1: Sealing Air Preheater Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33AA401YQ01 | B1LBG33AA401 | YQ01 | B1: Sealing Air Prehtr CV | B1: Sealing Air Preheater Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33CF001AXQ01 | B1LBG33CF001A | XQ01 | B1: Sealing Air Prehtr Flow 1 | B1: Sealing Air Preheater Flow 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33CF001BXQ01 | B1LBG33CF001B | XQ01 | B1: Sealing Air Prehtr Flow 2 | B1: Sealing Air Preheater Flow 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33CP001XQ01 | B1LBG33CP001 | XQ01 | B1: Sealing Air Prehtr Press | B1: Sealing Air Preheater Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33CT001XQ01 | B1LBG33CT001 | XQ01 | B1: Sealing Air Prehtr Temp | B1: Sealing Air Preheater Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LBG33CT002XQ01 | B1LBG33CT002 | XQ01 | B1: Sealing Air Prehtr Pot Temp | B1: Sealing Air Preheater Pot Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCA20CF001AXQ01 | B1LCA20CF001A | XQ01 | B1: ScrubStg1Que Flow 1 | B1: Scrubber Condensate Preheater Flow 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCA20CF001BXQ01 | B1LCA20CF001B | XQ01 | B1: ScrubStg1Que Flow 2 | B1: Scrubber Condensate Preheater Flow 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCA30AA301XB01 | B1LCA30AA301 | XB01 | B1: Econr Cool Ckt By-pass IV | B1: Economizer Cooling Circuit By-pass Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCA30AA301XB02 | B1LCA30AA301 | XB02 | B1: Econr Cool Ckt By-pass IV | B1: Economizer Cooling Circuit By-pass Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCA30AA301YB02 | B1LCA30AA301 | YB02 | B1: Econr Cool Ckt By-pass IV | B1: Economizer Cooling Circuit By-pass Isolation Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCA30AA302XB01 | B1LCA30AA302 | XB01 | B1: Intmd Conds Htr to Econr Cool Ckt Pmps IV | B1: Intermediate Condensate Heater to Economizer Cooling Circuit Pumps Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCA30AA302XB02 | B1LCA30AA302 | XB02 | B1: Intmd Conds Htr to Econr Cool Ckt Pmps IV | B1: Intermediate Condensate Heater to Economizer Cooling Circuit Pumps Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCA30AA302YB01 | B1LCA30AA302 | YB01 | B1: Intmd Conds Htr to Econr Cool Ckt Pmps IV | B1: Intermediate Condensate Heater to Economizer Cooling Circuit Pumps Isolation Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCA30CP001XQ01 | B1LCA30CP001 | XQ01 | B1: Econr Cool Ckt Pmps Disch Press | B1: Economizer Cooling Circuit Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCA30CT001XQ01 | B1LCA30CT001 | XQ01 | B1: Econr Cool Ckt Pmps Inl Temp | B1: Economizer Cooling Circuit Pumps Inlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCA30CT002XQ01 | B1LCA30CT002 | XQ01 | B1: Conds PreHtg Econr Outl Temp | B1: Condensate PreHeating Economizer Outlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN40AA301XB01 | B1LCN40AA301 | XB01 | B1: LP Pri AirPreHtr Lvl MOV | B1: LP Primary Air Preheater Level Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN40AA301XB02 | B1LCN40AA301 | XB02 | B1: LP Pri AirPreHtr Lvl MOV | B1: LP Primary Air Preheater Level Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN40AA301XB07 | B1LCN40AA301 | XB07 | B1: LP Pri AirPreHtr Lvl MOV | B1: LP Primary Air Preheater Level Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN40AA301XB23 | B1LCN40AA301 | XB23 | B1: LP Pri AirPreHtr Lvl MOV | B1: LP Primary Air Preheater Level Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN40AA301XQ13 | B1LCN40AA301 | XQ13 | B1: LP Pri AirPreHtr Lvl MOV | B1: LP Primary Air Preheater Level Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN40AA301YB01 | B1LCN40AA301 | YB01 | B1: LP Pri AirPreHtr Lvl MOV | B1: LP Primary Air Preheater Level Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN40AA301YB02 | B1LCN40AA301 | YB02 | B1: LP Pri AirPreHtr Lvl MOV | B1: LP Primary Air Preheater Level Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN40AA401XQ13 | B1LCN40AA401 | XQ13 | B1: LP Pri AirPreHtr Lvl CV | B1: LP Primary Air Preheater Level Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN40AA401YQ01 | B1LCN40AA401 | YQ01 | B1: LP Pri AirPreHtr Lvl CV | B1: LP Primary Air Preheater Level Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN40CF001AXQ01 | B1LCN40CF001A | XQ01 | B1: LP Pri AirPreHtr to Blr Cnd Rtn Tnk Flow 1 | B1: LP Primary Air Preheater to Boiler Condensate Return Tank Flow 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN40CF001BXQ01 | B1LCN40CF001B | XQ01 | B1: LP Pri AirPreHtr to Blr Cnd Rtn Tnk Flow 2 | B1: LP Primary Air Preheater to Boiler Condensate Return Tank Flow 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN50AA301XB01 | B1LCN50AA301 | XB01 | B1: LP Sec AirPreHtr Lvl MOV | B1: LP Secondary Air Preheater Level Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN50AA301XB02 | B1LCN50AA301 | XB02 | B1: LP Sec AirPreHtr Lvl MOV | B1: LP Secondary Air Preheater Level Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN50AA301XB07 | B1LCN50AA301 | XB07 | B1: LP Sec AirPreHtr Lvl MOV | B1: LP Secondary Air Preheater Level Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN50AA301XB23 | B1LCN50AA301 | XB23 | B1: LP Sec AirPreHtr Lvl MOV | B1: LP Secondary Air Preheater Level Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN50AA301XQ13 | B1LCN50AA301 | XQ13 | B1: LP Sec AirPreHtr Lvl MOV | B1: LP Secondary Air Preheater Level Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN50AA301YB01 | B1LCN50AA301 | YB01 | B1: LP Sec AirPreHtr Lvl MOV | B1: LP Secondary Air Preheater Level Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN50AA301YB02 | B1LCN50AA301 | YB02 | B1: LP Sec AirPreHtr Lvl MOV | B1: LP Secondary Air Preheater Level Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN50AA401XQ13 | B1LCN50AA401 | XQ13 | B1: LP Sec AirPreHtr Lvl CV | B1: LP Secondary Air Preheater Level Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN50AA401YQ01 | B1LCN50AA401 | YQ01 | B1: LP Sec AirPreHtr Lvl CV | B1: LP Secondary Air Preheater Level Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN50CF001AXQ01 | B1LCN50CF001A | XQ01 | B1: LP Sec AirPreHtr to Blr Cnd Rtn Tnk Flow 1 | B1: LP Secondary Air Preheater to Boiler Condensate Return Tank Flow 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN50CF001BXQ01 | B1LCN50CF001B | XQ01 | B1: LP Sec AirPreHtr to Blr Cnd Rtn Tnk Flow 2 | B1: LP Secondary Air Preheater to Boiler Condensate Return Tank Flow 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN60CP001XQ01 | B1LCN60CP001 | XQ01 | B1: LP Cond Seal AirPreHtr to Blr Cnd Rtn Tnk Press | B1: LP Condensate Seal Air Preheater to Boiler Condensate Return Tank Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN60CT001XQ01 | B1LCN60CT001 | XQ01 | B1: LP Cond Seal AirPreHtr to Blr Cnd Rtn Tnk Temp | B1: LP Condensate Seal Air Preheater to Boiler Condensate Return Tank Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN70AA301XB01 | B1LCN70AA301 | XB01 | B1: HP Pri AirPreHtr Lvl MOV | B1: HP Primary Air Preheater Level Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN70AA301XB02 | B1LCN70AA301 | XB02 | B1: HP Pri AirPreHtr Lvl MOV | B1: HP Primary Air Preheater Level Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN70AA301XB07 | B1LCN70AA301 | XB07 | B1: HP Pri AirPreHtr Lvl MOV | B1: HP Primary Air Preheater Level Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN70AA301XB23 | B1LCN70AA301 | XB23 | B1: HP Pri AirPreHtr Lvl MOV | B1: HP Primary Air Preheater Level Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN70AA301XQ13 | B1LCN70AA301 | XQ13 | B1: HP Pri AirPreHtr Lvl MOV | B1: HP Primary Air Preheater Level Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN70AA301YB01 | B1LCN70AA301 | YB01 | B1: HP Pri AirPreHtr Lvl MOV | B1: HP Primary Air Preheater Level Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN70AA301YB02 | B1LCN70AA301 | YB02 | B1: HP Pri AirPreHtr Lvl MOV | B1: HP Primary Air Preheater Level Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN70AA401XQ13 | B1LCN70AA401 | XQ13 | B1: HP Pri AirPreHtr Lvl CV | B1: HP Primary Air Preheater Level Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN70AA401YQ01 | B1LCN70AA401 | YQ01 | B1: HP Pri AirPreHtr Lvl CV | B1: HP Primary Air Preheater Level Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN70CF001AXQ01 | B1LCN70CF001A | XQ01 | B1: HP Pri AirPreHtr to Blr Cnd Rtn Tnk Flow 1 | B1: HP Primary Air Preheater to Boiler Condensate Return Tank Flow 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN70CF001BXQ01 | B1LCN70CF001B | XQ01 | B1: HP Pri AirPreHtr to Blr Cnd Rtn Tnk Flow 2 | B1: HP Primary Air Preheater to Boiler Condensate Return Tank Flow 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN70CP001XQ01 | B1LCN70CP001 | XQ01 | B1: HP Pri AirPreHtr to Blr Cnd Rtn Tnk Press 1 | B1: HP Primary Air Preheater to Boiler Condensate Return Tank Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN70CP002XQ01 | B1LCN70CP002 | XQ01 | B1: HP Pri AirPreHtr to Blr Cnd Rtn Tnk Press 1 | B1: HP Primary Air Preheater to Boiler Condensate Return Tank Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN80AA401XQ13 | B1LCN80AA401 | XQ13 | B1: Stm FluGas HX Cnd Accu Lvl CV | B1: Steam Flue Gas Heat Exchanger Condensate Accumulator Level Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN80AA401YQ01 | B1LCN80AA401 | YQ01 | B1: Stm FluGas HX Cnd Accu Lvl CV | B1: Steam Flue Gas Heat Exchanger Condensate Accumulator Level Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN80CL001AXQ01 | B1LCN80CL001A | XQ01 | B1: Stm FluGas HX Cnd Accu Lvl 1 | B1: Steam Flue Gas Heat Exchanger Condensate Accumulator Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN80CL001BXQ01 | B1LCN80CL001B | XQ01 | B1: Stm FluGas HX Cnd Accu Lvl 2 | B1: Steam Flue Gas Heat Exchanger Condensate Accumulator Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN80CP001AXQ01 | B1LCN80CP001A | XQ01 | B1: Stm FluGas HX Cnd Accu Press 1 | B1: Steam Flue Gas Heat Exchanger Condensate Accumulator Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN80CP001BXQ01 | B1LCN80CP001B | XQ01 | B1: Stm FluGas HX Cnd Accu Press 2 | B1: Steam Flue Gas Heat Exchanger Condensate Accumulator Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN80CP010XQ01 | B1LCN80CP010 | XQ01 | B1: Stm FluGas HX to Cnd Accu Press | B1: Steam Flue Gas Heat Exchanger to Condensate Accumulator Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN80CP020XQ01 | B1LCN80CP020 | XQ01 | B1: Cnd FluGas HX Outl Press | B1: Condensate Flue Gas Heat Exchanger Outlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN80CP030XQ01 | B1LCN80CP030 | XQ01 | B1: Cnd FluGas HX to Blr Cnd Rtn Tnk Press | B1: Condensate Flue Gas Heat Exchanger to Boiler Condensate Return Tank Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN80CT001XQ01 | B1LCN80CT001 | XQ01 | B1: Stm FluGas HX Cnd Accu Bottom Temp 1 | B1: Steam Flue Gas Heat Exchanger Condensate Accumulator Bottom Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN80CT002XQ01 | B1LCN80CT002 | XQ01 | B1: Stm FluGas HX Cnd Accu Bottom Temp 2 | B1: Steam Flue Gas Heat Exchanger Condensate Accumulator Bottom Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN80CT010XQ01 | B1LCN80CT010 | XQ01 | B1: Stm FluGas HX to Cnd Accu Temp | B1: Steam Flue Gas Heat Exchanger to Condensate Accumulator Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN80CT020XQ01 | B1LCN80CT020 | XQ01 | B1: Cnd FluGas HX Outl Temp | B1: Condensate Flue Gas Heat Exchanger Outlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN80CT030XQ01 | B1LCN80CT030 | XQ01 | B1: Cnd FluGas HX to Blr Cnd Rtn Tnk Temp | B1: Condensate Flue Gas Heat Exchanger to Boiler Condensate Return Tank Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN81AA401XQ13 | B1LCN81AA401 | XQ13 | B1: Stm FluGas HX Cnd Accu Press CV | B1: Steam Flue Gas Heat Exchanger Condensate Accumulator Pressure Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN81AA401YQ01 | B1LCN81AA401 | YQ01 | B1: Stm FluGas HX Cnd Accu Press CV | B1: Steam Flue Gas Heat Exchanger Condensate Accumulator Pressure Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN81CP001XQ01 | B1LCN81CP001 | XQ01 | B1: Stm FluGas HX Cnd Accu to Cnd Rtn Tnk Press | B1: Steam Flue Gas Heat Exchanger Condensate Accumulator to Condensate Return Tank Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCN81CT001XQ01 | B1LCN81CT001 | XQ01 | B1: Stm FluGas HX Cnd Accu to Cnd Rtn Tnk Temp | B1: Steam Flue Gas Heat Exchanger Condensate Accumulator to Condensate Return Tank Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCQ10CP001XQ01 | B1LCQ10CP001 | XQ01 | B1: BlwDn Pmps Suct Press | B1: Blowdown Pumps Suction Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCQ10CT001AXQ01 | B1LCQ10CT001A | XQ01 | B1: BlwDn Pmps Suct Temp 1 | B1: Blowdown Pumps Suction Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCQ10CT001BXQ01 | B1LCQ10CT001B | XQ01 | B1: BlwDn Pmps Suct Temp 2 | B1: Blowdown Pumps Suction Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCQ11CP001XQ01 | B1LCQ11CP001 | XQ01 | B1: BlwDn Pmp1 Suct Filtr DP | B1: Blowdown Pump 1 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCQ12CP001XQ01 | B1LCQ12CP001 | XQ01 | B1: BlwDn Pmp2 Suct Filtr DP | B1: Blowdown Pump 2 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCQ13CP001XQ01 | B1LCQ13CP001 | XQ01 | B1: Emerg BlwDn Pmp Suct Press | B1: Emergency Blowdown Pump Suction Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCQ13CP002XQ01 | B1LCQ13CP002 | XQ01 | B1: Emerg BlwDn Pmp Suct Filtr DP | B1: Emergency Blowdown Pump Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCQ13CT001AXQ01 | B1LCQ13CT001A | XQ01 | B1: Emerg BlwDn Pmp Suct Temp 1 | B1: Emergency Blowdown Pump Suction Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCQ13CT001BXQ01 | B1LCQ13CT001B | XQ01 | B1: Emerg BlwDn Pmp Suct Temp 2 | B1: Emergency Blowdown Pump Suction Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCQ15AA401XQ13 | B1LCQ15AA401 | XQ13 | B1: Emerg BlwDn Pmp Disch CV | B1: Emergency Blowdown Pump Discharge Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCQ15AA401YQ01 | B1LCQ15AA401 | YQ01 | B1: Emerg BlwDn Pmp Disch CV | B1: Emergency Blowdown Pump Discharge Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCQ15CP001XQ01 | B1LCQ15CP001 | XQ01 | B1: Emerg BlwDn Pmp Disch Press | B1: Emergency Blowdown Pump Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCQ25AA401XQ13 | B1LCQ25AA401 | XQ13 | B1: BlwDn Pmps Disch CV | B1: Blowdown Pumps Discharge Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCQ25AA401YQ01 | B1LCQ25AA401 | YQ01 | B1: BlwDn Pmps Disch CV | B1: Blowdown Pumps Discharge Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1LCQ25CP001XQ01 | B1LCQ25CP001 | XQ01 | B1: BlwDn Pmps Disch Press | B1: Blowdown Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1MAN10AA301XB01 | B1MAN10AA301 | XB01 | B1: MS Pot Inl Bypass CV Drn MOV | B1: Main Steam Pot Inlet Bypass Control Valve Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1MAN10AA301XB02 | B1MAN10AA301 | XB02 | B1: MS Pot Inl Bypass CV Drn MOV | B1: Main Steam Pot Inlet Bypass Control Valve Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1MAN10AA301XB07 | B1MAN10AA301 | XB07 | B1: MS Pot Inl Bypass CV Drn MOV | B1: Main Steam Pot Inlet Bypass Control Valve Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1MAN10AA301XB23 | B1MAN10AA301 | XB23 | B1: MS Pot Inl Bypass CV Drn MOV | B1: Main Steam Pot Inlet Bypass Control Valve Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1MAN10AA301XQ13 | B1MAN10AA301 | XQ13 | B1: MS Pot Inl Bypass CV Drn MOV | B1: Main Steam Pot Inlet Bypass Control Valve Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1MAN10AA301YB01 | B1MAN10AA301 | YB01 | B1: MS Pot Inl Bypass CV Drn MOV | B1: Main Steam Pot Inlet Bypass Control Valve Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1MAN10AA301YB02 | B1MAN10AA301 | YB02 | B1: MS Pot Inl Bypass CV Drn MOV | B1: Main Steam Pot Inlet Bypass Control Valve Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1MAN10AA401XQ13 | B1MAN10AA401 | XQ13 | B1: Main Steam Bypass CV | B1: Main Steam Bypass Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1MAN10AA401YQ01 | B1MAN10AA401 | YQ01 | B1: Main Steam Bypass CV | B1: Main Steam Bypass Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1MAN10CP001AXQ01 | B1MAN10CP001A | XQ01 | B1: MS Bypass to ACC Press 1 | B1: Main Steam Bypass to Air Cooled Condenser Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1MAN10CP001BXQ01 | B1MAN10CP001B | XQ01 | B1: MS Bypass to ACC Press 2 | B1: Main Steam Bypass to Air Cooled Condenser Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1MAN10CT001AXQ01 | B1MAN10CT001A | XQ01 | B1: MS Bypass to ACC Temp 1 | B1: Main Steam Bypass to Air Cooled Condenser Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1MAN10CT001BXQ01 | B1MAN10CT001B | XQ01 | B1: MS Bypass to ACC Temp 2 | B1: Main Steam Bypass to Air Cooled Condenser Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1MAN10CT001XQ01 | B1MAN10CT001 | XQ01 | B1: MS Pot Inl Bypass Temp | B1: Main Steam Pot Inlet Bypass Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1PGB21CT001XQ01 | B1PGB21CT001 | XQ01 | B1: FdHoprCoolSyst to FFC Temp | B1: Feed Hopper Cooling System Steam Turbine to Fin Fan Coolers Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1PGB22CT001XQ01 | B1PGB22CT001 | XQ01 | B1: Comb Cam1 to FFC Temp | B1: Combustion Camera 1 to Fin Fan Coolers Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1PGB23CT001XQ01 | B1PGB23CT001 | XQ01 | B1: Comb Cam2 to FFC Temp | B1: Combustion Camera 2 to Fin Fan Coolers Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B1PGB24CT001XQ01 | B1PGB24CT001 | XQ01 | B1: HydrcStn to FFC Temp | B1: Hydraulic Station to Fin Fan Coolers Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B1QUB10CQ001XQ01 | B1QUB10CQ001 | XQ01 | B1: Live Steam DC | B1: Live Steam DC | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B1QUB10CQ002XQ01 | B1QUB10CQ002 | XQ01 | B1: Live Steam AC | B1: Live Steam AC | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B1QUB10CQ003XQ01 | B1QUB10CQ003 | XQ01 | B1: Live Steam SIO2 | B1: Live Steam SIO2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B1QUB10CQ004XQ01 | B1QUB10CQ004 | XQ01 | B1: Live Steam DCC | B1: Live Steam DCC | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B1QUH30CQ001XQ01 | B1QUH30CQ001 | XQ01 | B1: Boiler Water DC | B1: Boiler Water DC | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B1QUH30CQ002XQ01 | B1QUH30CQ002 | XQ01 | B1: Boiler Water AC | B1: Boiler Water AC | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B1QUH30CQ003XQ01 | B1QUH30CQ003 | XQ01 | B1: Boiler Water PH | B1: Boiler Water PH | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2EKG01AA001XB01 | B2EKG01AA001 | XB01 | Natural Gas Line 2 IV | Natural Gas Line 2 Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000011 - Natural Gas | NPE7-EAI-41XX-XXX-PP-XA-007643 | NPE7-EAI-41XX-XXX-PP-XA-007646 | NPE7-EAI-41XX-XXX-IM-XA-007643 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2EKG01AA001XB02 | B2EKG01AA001 | XB02 | Natural Gas Line 2 IV | Natural Gas Line 2 Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000011 - Natural Gas | NPE7-EAI-41XX-XXX-PP-XA-007643 | NPE7-EAI-41XX-XXX-PP-XA-007646 | NPE7-EAI-41XX-XXX-IM-XA-007643 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2GHE10CL001AXQ01 | B2GHE10CL001A | XQ01 | B2: Proc Wtr Tnk Blr Lvl 1 | B2: Process Water Tank Boiler Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2GHE10CL001BXQ01 | B2GHE10CL001B | XQ01 | B2: Proc Wtr Tnk Blr Lvl 2 | B2: Process Water Tank Boiler Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2GHE11CP001XQ01 | B2GHE11CP001 | XQ01 | B2: Proc Wtr Pmp1 Suct Fltr DP | B2: Process Water Pump 1 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2GHE12CP001XQ01 | B2GHE12CP001 | XQ01 | B2: Proc Wtr Pmp2 Suct Fltr DP | B2: Process Water Pump 2 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2GHE20CP001XQ01 | B2GHE20CP001 | XQ01 | B2: Proc Wtr Pmps Disch Press | B2: Process Water Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000019 - Process Water | NPE7-EAI-41XX-XXX-PP-XA-000120 | NPE7-EAI-41XX-XXX-PP-XA-007640 | NPE7-EAI-41XX-XXX-IM-XA-000121 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2HAD50AA301XB01 | B2HAD50AA301 | XB01 | B2: Blr to FluGas HtExchg Stm MOV | B2: Boiler to Flue Gas Heat Exchanger Steam Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2HAD50AA301XB02 | B2HAD50AA301 | XB02 | B2: Blr to FluGas HtExchg Stm MOV | B2: Boiler to Flue Gas Heat Exchanger Steam Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2HAD50AA301XB07 | B2HAD50AA301 | XB07 | B2: Blr to FluGas HtExchg Stm MOV | B2: Boiler to Flue Gas Heat Exchanger Steam Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2HAD50AA301XB23 | B2HAD50AA301 | XB23 | B2: Blr to FluGas HtExchg Stm MOV | B2: Boiler to Flue Gas Heat Exchanger Steam Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2HAD50AA301YB01 | B2HAD50AA301 | YB01 | B2: Blr to FluGas HtExchg Stm MOV | B2: Boiler to Flue Gas Heat Exchanger Steam Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2HAD50AA301YB02 | B2HAD50AA301 | YB02 | B2: Blr to FluGas HtExchg Stm MOV | B2: Boiler to Flue Gas Heat Exchanger Steam Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2HAD50AA302XB01 | B2HAD50AA302 | XB01 | B2: BlrDrm Pot B2HAD50 Drn Vlv | B2: Boiler Drum Pot B2HAD50 Drain Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2HAD50AA302XB02 | B2HAD50AA302 | XB02 | B2: BlrDrm Pot B2HAD50 Drn Vlv | B2: Boiler Drum Pot B2HAD50 Drain Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2HAD50AA302YB01 | B2HAD50AA302 | YB01 | B2: BlrDrm Pot B2HAD50 Drn Vlv | B2: Boiler Drum Pot B2HAD50 Drain Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2HAD50AA401XQ13 | B2HAD50AA401 | XQ13 | B2: Blr to FluGas HtExchg Stm CV | B2: Boiler to Flue Gas Heat Exchanger Steam Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2HAD50AA401YQ01 | B2HAD50AA401 | YQ01 | B2: Blr to FluGas HtExchg Stm CV | B2: Boiler to Flue Gas Heat Exchanger Steam Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2HAD50CL001XG01 | B2HAD50CL001 | XG01 | B2: BlrDrm Pot B2HAD50 Lvl Sw | B2: Boiler Drum Pot B2HAD50 Level Switch | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | LS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2HAD50CL002XG01 | B2HAD50CL002 | XG01 | B2: BlrDrm Pot B2HAD50 Lvl Sw | B2: Boiler Drum Pot B2HAD50 Level Switch | high | n high |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | LS |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2HAD50CP001XQ01 | B2HAD50CP001 | XQ01 | B2: Blr to FluGas HtExchg Stm Press | B2: Boiler to Flue Gas Heat Exchanger Steam Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2HAD50CT001XQ01 | B2HAD50CT001 | XQ01 | B2: Blr to FluGas HtExchg Stm Temp | B2: Boiler to Flue Gas Heat Exchanger Steam Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CEMS Supplier | B2HNE10CP001XQ01 | B2HNE10CP001 | XQ01 | B2: CEMS Interface | B2: CEMS Interface | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41CX-XXX-PD-XA-000016 - Stack/CEMS | NPE7-EAI-41XX-XXX-PP-XA-007619 | NPE7-EAI-41XX-XXX-PP-XA-007639 | NPE7-EAI-41XX-XXX-IM-XA-007617 | CEMS | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CEMS Supplier | B2HNE10CT001XQ01 | B2HNE10CT001 | XQ01 | B2: CEMS Interface | B2: CEMS Interface | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41CX-XXX-PD-XA-000016 - Stack/CEMS | NPE7-EAI-41XX-XXX-PP-XA-007619 | NPE7-EAI-41XX-XXX-PP-XA-007639 | NPE7-EAI-41XX-XXX-IM-XA-007617 | CEMS | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CEMS Supplier | B2HNE10GH001XB01 | B2HNE10GH001 | XB01 | B2: CEMS Interface | B2: CEMS Interface | in Operation |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41CX-XXX-PD-XA-000016 - Stack/CEMS | NPE7-EAI-41XX-XXX-PP-XA-007619 | NPE7-EAI-41XX-XXX-PP-XA-007639 | NPE7-EAI-41XX-XXX-IM-XA-007617 | CEMS | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CEMS Supplier | B2HNE10GH001XB04 | B2HNE10GH001 | XB04 | B2: CEMS Interface | B2: CEMS Interface | In Calib/Mainten Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41CX-XXX-PD-XA-000016 - Stack/CEMS | NPE7-EAI-41XX-XXX-PP-XA-007619 | NPE7-EAI-41XX-XXX-PP-XA-007639 | NPE7-EAI-41XX-XXX-IM-XA-007617 | CEMS | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CEMS Supplier | B2HNE10GH001XB31 | B2HNE10GH001 | XB31 | B2: CEMS Interface | B2: CEMS Interface | No General Alarm | General Alarm |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41CX-XXX-PD-XA-000016 - Stack/CEMS | NPE7-EAI-41XX-XXX-PP-XA-007619 | NPE7-EAI-41XX-XXX-PP-XA-007639 | NPE7-EAI-41XX-XXX-IM-XA-007617 | CEMS | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
CEMS Supplier | B2HNE10GH001XB33 | B2HNE10GH001 | XB33 | B2: CEMS Interface | B2: CEMS Interface | No Emission Limit Alarm | Emission Limit Alarm |  |  | DI | 24VDC | S |  |  | B0CRM01GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41CX-XXX-PD-XA-000016 - Stack/CEMS | NPE7-EAI-41XX-XXX-PP-XA-007619 | NPE7-EAI-41XX-XXX-PP-XA-007639 | NPE7-EAI-41XX-XXX-IM-XA-007617 | CEMS | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LAC40CP001XQ01 | B2LAC40CP001 | XQ01 | B2: FW Pmps to Blr Press | B2: Feedwater Pumps to Boiler Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LAC40CT001XQ01 | B2LAC40CT001 | XQ01 | B2: FW Pmps to Blr Temp | B2: Feedwater Pumps to Boiler Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LAF31AA301XB01 | B2LAF31AA301 | XB01 | B2: Bypass CV Attemp Water IV | B2: Bypass Control Valve Attemperation Water Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LAF31AA301XB02 | B2LAF31AA301 | XB02 | B2: Bypass CV Attemp Water IV | B2: Bypass Control Valve Attemperation Water Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LAF31AA301YB01 | B2LAF31AA301 | YB01 | B2: Bypass CV Attemp Water IV | B2: Bypass Control Valve Attemperation Water Isolation Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LAF31AA401XQ13 | B2LAF31AA401 | XQ13 | B2: Main Steam Bypass Attemp CV | B2: Main Steam Bypass Attemperation Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LAF31AA401YQ01 | B2LAF31AA401 | YQ01 | B2: Main Steam Bypass Attemp CV | B2: Main Steam Bypass Attemperation Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LAF31CF001AXQ01 | B2LAF31CF001A | XQ01 | B2: MS Bypass Attemp Flow 1 | B2: Main Steam Bypass Attemperation Flow 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LAF31CF001BXQ01 | B2LAF31CF001B | XQ01 | B2: MS Bypass Attemp Flow 2 | B2: Main Steam Bypass Attemperation Flow 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LAF31CP001XQ01 | B2LAF31CP001 | XQ01 | B2: MS Byp Attemp CV Inl Press | B2: Main Steam By-pass Attemperation Control Valve Inlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LAF31CP002XQ01 | B2LAF31CP002 | XQ01 | B2: MS Byp Attemp CV Outl Press | B2: Main Steam By-pass Attemperation Control Valve Outlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LAF31CP003XQ01 | B2LAF31CP003 | XQ01 | B2: MS Byp Attemp Fltr DP | B2: Main Steam By-pass Attemperation Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA10AA301XB01 | B2LBA10AA301 | XB01 | B2: MS Isol MOV | B2: Main Steam Isolation Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA10AA301XB02 | B2LBA10AA301 | XB02 | B2: MS Isol MOV | B2: Main Steam Isolation Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA10AA301XB07 | B2LBA10AA301 | XB07 | B2: MS Isol MOV | B2: Main Steam Isolation Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA10AA301XB23 | B2LBA10AA301 | XB23 | B2: MS Isol MOV | B2: Main Steam Isolation Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA10AA301YB01 | B2LBA10AA301 | YB01 | B2: MS Isol MOV | B2: Main Steam Isolation Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA10AA301YB02 | B2LBA10AA301 | YB02 | B2: MS Isol MOV | B2: Main Steam Isolation Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA10AA302XB01 | B2LBA10AA302 | XB01 | B2: MS Pot B2LBA10 Drn MOV | B2: Main Steam Pot B2LBA10 Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA10AA302XB02 | B2LBA10AA302 | XB02 | B2: MS Pot B2LBA10 Drn MOV | B2: Main Steam Pot B2LBA10 Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA10AA302XB07 | B2LBA10AA302 | XB07 | B2: MS Pot B2LBA10 Drn MOV | B2: Main Steam Pot B2LBA10 Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA10AA302XB23 | B2LBA10AA302 | XB23 | B2: MS Pot B2LBA10 Drn MOV | B2: Main Steam Pot B2LBA10 Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA10AA302XQ13 | B2LBA10AA302 | XQ13 | B2: MS Pot B2LBA10 Drn MOV | B2: Main Steam Pot B2LBA10 Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA10AA302YB01 | B2LBA10AA302 | YB01 | B2: MS Pot B2LBA10 Drn MOV | B2: Main Steam Pot B2LBA10 Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA10AA302YB02 | B2LBA10AA302 | YB02 | B2: MS Pot B2LBA10 Drn MOV | B2: Main Steam Pot B2LBA10 Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA10CP001AXQ01 | B2LBA10CP001A | XQ01 | B2: MS from Boiler Press 1 | B2: Main Steam from Boiler Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA10CP001BXQ01 | B2LBA10CP001B | XQ01 | B2: MS from Boiler Press 2 | B2: Main Steam from Boiler Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA10CT001AXQ01 | B2LBA10CT001A | XQ01 | B2: MS from Boiler Temp 1 | B2: Main Steam from Boiler Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA10CT001BXQ01 | B2LBA10CT001B | XQ01 | B2: MS from Boiler Temp 2 | B2: Main Steam from Boiler Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA10CT001CXQ01 | B2LBA10CT001C | XQ01 | B2: MS from Boiler Temp 3 | B2: Main Steam from Boiler Temperature 3 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | C | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA10CT001XQ01 | B2LBA10CT001 | XQ01 | B2: MS Pot B2LBA10 Temp | B2: Main Steam Pot B2LBA10 Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA20AA301XB01 | B2LBA20AA301 | XB01 | B2: MS Pot Bfr Bypass Drn MOV | B2: Main Steam Pot Before Bypass Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA20AA301XB02 | B2LBA20AA301 | XB02 | B2: MS Pot Bfr Bypass Drn MOV | B2: Main Steam Pot Before Bypass Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA20AA301XB07 | B2LBA20AA301 | XB07 | B2: MS Pot Bfr Bypass Drn MOV | B2: Main Steam Pot Before Bypass Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA20AA301XB23 | B2LBA20AA301 | XB23 | B2: MS Pot Bfr Bypass Drn MOV | B2: Main Steam Pot Before Bypass Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA20AA301XQ13 | B2LBA20AA301 | XQ13 | B2: MS Pot Bfr Bypass Drn MOV | B2: Main Steam Pot Before Bypass Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA20AA301YB01 | B2LBA20AA301 | YB01 | B2: MS Pot Bfr Bypass Drn MOV | B2: Main Steam Pot Before Bypass Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA20AA301YB02 | B2LBA20AA301 | YB02 | B2: MS Pot Bfr Bypass Drn MOV | B2: Main Steam Pot Before Bypass Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBA20CT001XQ01 | B2LBA20CT001 | XQ01 | B2: MS Pot Bfr Bypass Temp | B2: Main Steam Pot Before Bypass Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30AA301XB01 | B2LBG30AA301 | XB01 | B2: AuxStm to AirPrehtr Byp MOV | B2: Aux Steam to Air Preheater By-pass Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30AA301XB02 | B2LBG30AA301 | XB02 | B2: AuxStm to AirPrehtr Byp MOV | B2: Aux Steam to Air Preheater By-pass Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30AA301XB07 | B2LBG30AA301 | XB07 | B2: AuxStm to AirPrehtr Byp MOV | B2: Aux Steam to Air Preheater By-pass Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30AA301XB23 | B2LBG30AA301 | XB23 | B2: AuxStm to AirPrehtr Byp MOV | B2: Aux Steam to Air Preheater By-pass Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30AA301XQ13 | B2LBG30AA301 | XQ13 | B2: AuxStm to AirPrehtr Byp MOV | B2: Aux Steam to Air Preheater By-pass Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30AA301YB01 | B2LBG30AA301 | YB01 | B2: AuxStm to AirPrehtr Byp MOV | B2: Aux Steam to Air Preheater By-pass Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30AA301YB02 | B2LBG30AA301 | YB02 | B2: AuxStm to AirPrehtr Byp MOV | B2: Aux Steam to Air Preheater By-pass Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30AA302XB01 | B2LBG30AA302 | XB01 | B2: AuxStm to AirPrehtr Pot Drn MOV | B2: Aux Steam to Air Preheater Pot Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30AA302XB02 | B2LBG30AA302 | XB02 | B2: AuxStm to AirPrehtr Pot Drn MOV | B2: Aux Steam to Air Preheater Pot Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30AA302XB07 | B2LBG30AA302 | XB07 | B2: AuxStm to AirPrehtr Pot Drn MOV | B2: Aux Steam to Air Preheater Pot Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30AA302XB23 | B2LBG30AA302 | XB23 | B2: AuxStm to AirPrehtr Pot Drn MOV | B2: Aux Steam to Air Preheater Pot Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30AA302XQ13 | B2LBG30AA302 | XQ13 | B2: AuxStm to AirPrehtr Pot Drn MOV | B2: Aux Steam to Air Preheater Pot Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30AA302YB01 | B2LBG30AA302 | YB01 | B2: AuxStm to AirPrehtr Pot Drn MOV | B2: Aux Steam to Air Preheater Pot Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30AA302YB02 | B2LBG30AA302 | YB02 | B2: AuxStm to AirPrehtr Pot Drn MOV | B2: Aux Steam to Air Preheater Pot Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30AA401XQ13 | B2LBG30AA401 | XQ13 | B2: AuxStm to AirPrehtr CV | B2: Aux Steam to Air Preheater Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30AA401YQ01 | B2LBG30AA401 | YQ01 | B2: AuxStm to AirPrehtr CV | B2: Aux Steam to Air Preheater Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30CF001AXQ01 | B2LBG30CF001A | XQ01 | B2: AuxStm to AirPrehtr Flow 1 | B2: Aux Steam to Air Preheater Flow 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30CF001BXQ01 | B2LBG30CF001B | XQ01 | B2: AuxStm to AirPrehtr Flow 2 | B2: Aux Steam to Air Preheater Flow 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30CP001XQ01 | B2LBG30CP001 | XQ01 | B2: AuxStm to AirPrehtr Press | B2: Aux Steam to Air Preheater Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30CT001AXQ01 | B2LBG30CT001A | XQ01 | B2: AuxStm to AirPrehtr Temp 1 | B2: Aux Steam to Air Preheater Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30CT001BXQ01 | B2LBG30CT001B | XQ01 | B2: AuxStm to AirPrehtr Temp 2 | B2: Aux Steam to Air Preheater Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG30CT002XQ01 | B2LBG30CT002 | XQ01 | B2: AuxStm to AirPrehtr Drn Temp | B2: Aux Steam to Air Preheater Drain Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG31AA301XB01 | B2LBG31AA301 | XB01 | B2: Blr to PriAirPrehtr Byp MOV | B2: Boiler to Primary Air Preheater By-pass Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG31AA301XB02 | B2LBG31AA301 | XB02 | B2: Blr to PriAirPrehtr Byp MOV | B2: Boiler to Primary Air Preheater By-pass Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG31AA301XB07 | B2LBG31AA301 | XB07 | B2: Blr to PriAirPrehtr Byp MOV | B2: Boiler to Primary Air Preheater By-pass Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG31AA301XB23 | B2LBG31AA301 | XB23 | B2: Blr to PriAirPrehtr Byp MOV | B2: Boiler to Primary Air Preheater By-pass Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG31AA301XQ13 | B2LBG31AA301 | XQ13 | B2: Blr to PriAirPrehtr Byp MOV | B2: Boiler to Primary Air Preheater By-pass Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG31AA301YB01 | B2LBG31AA301 | YB01 | B2: Blr to PriAirPrehtr Byp MOV | B2: Boiler to Primary Air Preheater By-pass Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG31AA301YB02 | B2LBG31AA301 | YB02 | B2: Blr to PriAirPrehtr Byp MOV | B2: Boiler to Primary Air Preheater By-pass Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG31AA302XB01 | B2LBG31AA302 | XB01 | B2: PriAirPrehtr to BlwDn Tnk MOV | B2: Primary Air Preheater to Blowdown Tank Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG31AA302XB02 | B2LBG31AA302 | XB02 | B2: PriAirPrehtr to BlwDn Tnk MOV | B2: Primary Air Preheater to Blowdown Tank Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG31AA302XB07 | B2LBG31AA302 | XB07 | B2: PriAirPrehtr to BlwDn Tnk MOV | B2: Primary Air Preheater to Blowdown Tank Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG31AA302XB23 | B2LBG31AA302 | XB23 | B2: PriAirPrehtr to BlwDn Tnk MOV | B2: Primary Air Preheater to Blowdown Tank Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG31AA302XQ13 | B2LBG31AA302 | XQ13 | B2: PriAirPrehtr to BlwDn Tnk MOV | B2: Primary Air Preheater to Blowdown Tank Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG31AA302YB01 | B2LBG31AA302 | YB01 | B2: PriAirPrehtr to BlwDn Tnk MOV | B2: Primary Air Preheater to Blowdown Tank Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG31AA302YB02 | B2LBG31AA302 | YB02 | B2: PriAirPrehtr to BlwDn Tnk MOV | B2: Primary Air Preheater to Blowdown Tank Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG31AA401XQ13 | B2LBG31AA401 | XQ13 | B2: Blr to PriAirPrehtr CV | B2: Boiler to Primary Air Preheater Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG31AA401YQ01 | B2LBG31AA401 | YQ01 | B2: Blr to PriAirPrehtr CV | B2: Boiler to Primary Air Preheater Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG31CP001XQ01 | B2LBG31CP001 | XQ01 | B2: Blr to PriAirPrehtr Byp Press | B2: Boiler to Primary Air Preheater By-pass Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG31CT001XQ01 | B2LBG31CT001 | XQ01 | B2: PriAirPrehtr to BlwDn Tnk Temp | B2: Primary Air Preheater to Blowdown Tank Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG32AA301XB01 | B2LBG32AA301 | XB01 | B2: Blr to SecAirPrehtr Byp MOV | B2: Boiler to Secondary Air Preheater By-pass Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG32AA301XB02 | B2LBG32AA301 | XB02 | B2: Blr to SecAirPrehtr Byp MOV | B2: Boiler to Secondary Air Preheater By-pass Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG32AA301XB07 | B2LBG32AA301 | XB07 | B2: Blr to SecAirPrehtr Byp MOV | B2: Boiler to Secondary Air Preheater By-pass Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG32AA301XB23 | B2LBG32AA301 | XB23 | B2: Blr to SecAirPrehtr Byp MOV | B2: Boiler to Secondary Air Preheater By-pass Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG32AA301XQ13 | B2LBG32AA301 | XQ13 | B2: Blr to SecAirPrehtr Byp MOV | B2: Boiler to Secondary Air Preheater By-pass Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG32AA301YB01 | B2LBG32AA301 | YB01 | B2: Blr to SecAirPrehtr Byp MOV | B2: Boiler to Secondary Air Preheater By-pass Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG32AA301YB02 | B2LBG32AA301 | YB02 | B2: Blr to SecAirPrehtr Byp MOV | B2: Boiler to Secondary Air Preheater By-pass Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG32AA302XB01 | B2LBG32AA302 | XB01 | B2: SecAirPrehtr to BlwDn Tnk MOV | B2: Secondary Air Preheater to Blowdown Tank Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG32AA302XB02 | B2LBG32AA302 | XB02 | B2: SecAirPrehtr to BlwDn Tnk MOV | B2: Secondary Air Preheater to Blowdown Tank Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG32AA302XB07 | B2LBG32AA302 | XB07 | B2: SecAirPrehtr to BlwDn Tnk MOV | B2: Secondary Air Preheater to Blowdown Tank Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG32AA302XB23 | B2LBG32AA302 | XB23 | B2: SecAirPrehtr to BlwDn Tnk MOV | B2: Secondary Air Preheater to Blowdown Tank Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG32AA302XQ13 | B2LBG32AA302 | XQ13 | B2: SecAirPrehtr to BlwDn Tnk MOV | B2: Secondary Air Preheater to Blowdown Tank Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG32AA302YB01 | B2LBG32AA302 | YB01 | B2: SecAirPrehtr to BlwDn Tnk MOV | B2: Secondary Air Preheater to Blowdown Tank Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG32AA302YB02 | B2LBG32AA302 | YB02 | B2: SecAirPrehtr to BlwDn Tnk MOV | B2: Secondary Air Preheater to Blowdown Tank Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG32AA401XQ13 | B2LBG32AA401 | XQ13 | B2: Blr to SecAirPrehtr CV | B2: Boiler to Secondary Air Preheater Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG32AA401YQ01 | B2LBG32AA401 | YQ01 | B2: Blr to SecAirPrehtr CV | B2: Boiler to Secondary Air Preheater Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG32CP001XQ01 | B2LBG32CP001 | XQ01 | B2: Blr to SecAirPrehtr Byp Press | B2: Boiler to Secondary Air Preheater By-pass Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG32CT001XQ01 | B2LBG32CT001 | XQ01 | B2: SecAirPrehtr to BlwDn Tnk Temp | B2: Secondary Air Preheater to Blowdown Tank Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA301XB01 | B2LBG33AA301 | XB01 | B2: Sealing Air Prehtr MOV | B2: Sealing Air Preheater Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA301XB02 | B2LBG33AA301 | XB02 | B2: Sealing Air Prehtr MOV | B2: Sealing Air Preheater Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA301XB07 | B2LBG33AA301 | XB07 | B2: Sealing Air Prehtr MOV | B2: Sealing Air Preheater Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA301XB23 | B2LBG33AA301 | XB23 | B2: Sealing Air Prehtr MOV | B2: Sealing Air Preheater Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA301YB01 | B2LBG33AA301 | YB01 | B2: Sealing Air Prehtr MOV | B2: Sealing Air Preheater Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA301YB02 | B2LBG33AA301 | YB02 | B2: Sealing Air Prehtr MOV | B2: Sealing Air Preheater Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA302XB01 | B2LBG33AA302 | XB01 | B2: Sealing Air Prehtr Byp MOV | B2: Sealing Air Preheater By-pass Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA302XB02 | B2LBG33AA302 | XB02 | B2: Sealing Air Prehtr Byp MOV | B2: Sealing Air Preheater By-pass Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA302XB07 | B2LBG33AA302 | XB07 | B2: Sealing Air Prehtr Byp MOV | B2: Sealing Air Preheater By-pass Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA302XB23 | B2LBG33AA302 | XB23 | B2: Sealing Air Prehtr Byp MOV | B2: Sealing Air Preheater By-pass Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA302XQ13 | B2LBG33AA302 | XQ13 | B2: Sealing Air Prehtr Byp MOV | B2: Sealing Air Preheater By-pass Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA302YB01 | B2LBG33AA302 | YB01 | B2: Sealing Air Prehtr Byp MOV | B2: Sealing Air Preheater By-pass Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA302YB02 | B2LBG33AA302 | YB02 | B2: Sealing Air Prehtr Byp MOV | B2: Sealing Air Preheater By-pass Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA303XB01 | B2LBG33AA303 | XB01 | B2: Sealing AirPrehtr Pot Drn MOV | B2: Sealing Air Preheater Pot Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA303XB02 | B2LBG33AA303 | XB02 | B2: Sealing AirPrehtr Pot Drn MOV | B2: Sealing Air Preheater Pot Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA303XB07 | B2LBG33AA303 | XB07 | B2: Sealing AirPrehtr Pot Drn MOV | B2: Sealing Air Preheater Pot Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA303XB23 | B2LBG33AA303 | XB23 | B2: Sealing AirPrehtr Pot Drn MOV | B2: Sealing Air Preheater Pot Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA303XQ13 | B2LBG33AA303 | XQ13 | B2: Sealing AirPrehtr Pot Drn MOV | B2: Sealing Air Preheater Pot Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA303YB01 | B2LBG33AA303 | YB01 | B2: Sealing AirPrehtr Pot Drn MOV | B2: Sealing Air Preheater Pot Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA303YB02 | B2LBG33AA303 | YB02 | B2: Sealing AirPrehtr Pot Drn MOV | B2: Sealing Air Preheater Pot Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA401XQ13 | B2LBG33AA401 | XQ13 | B2: Sealing Air Prehtr CV | B2: Sealing Air Preheater Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33AA401YQ01 | B2LBG33AA401 | YQ01 | B2: Sealing Air Prehtr CV | B2: Sealing Air Preheater Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33CF001AXQ01 | B2LBG33CF001A | XQ01 | B2: Sealing Air Prehtr Flow 1 | B2: Sealing Air Preheater Flow 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33CF001BXQ01 | B2LBG33CF001B | XQ01 | B2: Sealing Air Prehtr Flow 2 | B2: Sealing Air Preheater Flow 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33CP001XQ01 | B2LBG33CP001 | XQ01 | B2: Sealing Air Prehtr Press | B2: Sealing Air Preheater Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33CT001XQ01 | B2LBG33CT001 | XQ01 | B2: Sealing Air Prehtr Temp | B2: Sealing Air Preheater Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LBG33CT002XQ01 | B2LBG33CT002 | XQ01 | B2: Sealing Air Prehtr Pot Temp | B2: Sealing Air Preheater Pot Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCA20CF001AXQ01 | B2LCA20CF001A | XQ01 | B2: ScrubStg1Que Flow 1 | B2: Scrubber Condensate Preheater Flow 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCA20CF001BXQ01 | B2LCA20CF001B | XQ01 | B2: ScrubStg1Que Flow 2 | B2: Scrubber Condensate Preheater Flow 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCA30AA301XB01 | B2LCA30AA301 | XB01 | B2: Econr Cool Ckt By-pass IV | B2: Economizer Cooling Circuit By-pass Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCA30AA301XB02 | B2LCA30AA301 | XB02 | B2: Econr Cool Ckt By-pass IV | B2: Economizer Cooling Circuit By-pass Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCA30AA301YB02 | B2LCA30AA301 | YB02 | B2: Econr Cool Ckt By-pass IV | B2: Economizer Cooling Circuit By-pass Isolation Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCA30AA302XB01 | B2LCA30AA302 | XB01 | B2: Intmd Conds Htr to Econr Cool Ckt Pmps IV | B2: Intermediate Condensate Heater to Economizer Cooling Circuit Pumps Isolation Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCA30AA302XB02 | B2LCA30AA302 | XB02 | B2: Intmd Conds Htr to Econr Cool Ckt Pmps IV | B2: Intermediate Condensate Heater to Economizer Cooling Circuit Pumps Isolation Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCA30AA302YB01 | B2LCA30AA302 | YB01 | B2: Intmd Conds Htr to Econr Cool Ckt Pmps IV | B2: Intermediate Condensate Heater to Economizer Cooling Circuit Pumps Isolation Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCA30CP001XQ01 | B2LCA30CP001 | XQ01 | B2: Econr Cool Ckt Pmps Disch Press | B2: Economizer Cooling Circuit Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCA30CT001XQ01 | B2LCA30CT001 | XQ01 | B2: Econr Cool Ckt Pmps Inl Temp | B2: Economizer Cooling Circuit Pumps Inlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCA30CT002XQ01 | B2LCA30CT002 | XQ01 | B2: Conds PreHtg Econr Outl Temp | B2: Condensate PreHeating Economizer Outlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000008 - Condensate | NPE7-EAI-41XX-XXX-PP-XA-007603 | NPE7-EAI-41XX-XXX-PP-XA-007623 | NPE7-EAI-41XX-XXX-IM-XA-007652 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN40AA301XB01 | B2LCN40AA301 | XB01 | B1: LP Pri AirPreHtr Lvl MOV | B1: LP Primary Air Preheater Level Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN40AA301XB02 | B2LCN40AA301 | XB02 | B1: LP Pri AirPreHtr Lvl MOV | B1: LP Primary Air Preheater Level Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN40AA301XB07 | B2LCN40AA301 | XB07 | B1: LP Pri AirPreHtr Lvl MOV | B1: LP Primary Air Preheater Level Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN40AA301XB23 | B2LCN40AA301 | XB23 | B1: LP Pri AirPreHtr Lvl MOV | B1: LP Primary Air Preheater Level Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN40AA301XQ13 | B2LCN40AA301 | XQ13 | B1: LP Pri AirPreHtr Lvl MOV | B1: LP Primary Air Preheater Level Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN40AA301YB01 | B2LCN40AA301 | YB01 | B1: LP Pri AirPreHtr Lvl MOV | B1: LP Primary Air Preheater Level Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN40AA301YB02 | B2LCN40AA301 | YB02 | B1: LP Pri AirPreHtr Lvl MOV | B1: LP Primary Air Preheater Level Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN40AA401XQ13 | B2LCN40AA401 | XQ13 | B2: LP Pri AirPreHtr Lvl CV | B2: LP Primary Air Preheater Level Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN40AA401YQ01 | B2LCN40AA401 | YQ01 | B2: LP Pri AirPreHtr Lvl CV | B2: LP Primary Air Preheater Level Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN40CF001AXQ01 | B2LCN40CF001A | XQ01 | B2: LP Pri AirPreHtr to Blr Cnd Rtn Tnk Flow 1 | B2: LP Primary Air Preheater to Boiler Condensate Return Tank Flow 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN40CF001BXQ01 | B2LCN40CF001B | XQ01 | B2: LP Pri AirPreHtr to Blr Cnd Rtn Tnk Flow 2 | B2: LP Primary Air Preheater to Boiler Condensate Return Tank Flow 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN50AA301XB01 | B2LCN50AA301 | XB01 | B1: LP Sec AirPreHtr Lvl MOV | B1: LP Secondary Air Preheater Level Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN50AA301XB02 | B2LCN50AA301 | XB02 | B1: LP Sec AirPreHtr Lvl MOV | B1: LP Secondary Air Preheater Level Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN50AA301XB07 | B2LCN50AA301 | XB07 | B1: LP Sec AirPreHtr Lvl MOV | B1: LP Secondary Air Preheater Level Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN50AA301XB23 | B2LCN50AA301 | XB23 | B1: LP Sec AirPreHtr Lvl MOV | B1: LP Secondary Air Preheater Level Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN50AA301XQ13 | B2LCN50AA301 | XQ13 | B1: LP Sec AirPreHtr Lvl MOV | B1: LP Secondary Air Preheater Level Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN50AA301YB01 | B2LCN50AA301 | YB01 | B1: LP Sec AirPreHtr Lvl MOV | B1: LP Secondary Air Preheater Level Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN50AA301YB02 | B2LCN50AA301 | YB02 | B1: LP Sec AirPreHtr Lvl MOV | B1: LP Secondary Air Preheater Level Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN50AA401XQ13 | B2LCN50AA401 | XQ13 | B2: LP Sec AirPreHtr Lvl CV | B2: LP Secondary Air Preheater Level Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN50AA401YQ01 | B2LCN50AA401 | YQ01 | B2: LP Sec AirPreHtr Lvl CV | B2: LP Secondary Air Preheater Level Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN50CF001AXQ01 | B2LCN50CF001A | XQ01 | B2: LP Sec AirPreHtr to Blr Cnd Rtn Tnk Flow 1 | B2: LP Secondary Air Preheater to Boiler Condensate Return Tank Flow 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN50CF001BXQ01 | B2LCN50CF001B | XQ01 | B2: LP Sec AirPreHtr to Blr Cnd Rtn Tnk Flow 2 | B2: LP Secondary Air Preheater to Boiler Condensate Return Tank Flow 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN60CP001XQ01 | B2LCN60CP001 | XQ01 | B2: LP Cond Seal AirPreHtr to Blr Cnd Rtn Tnk Press | B2: LP Condensate Seal Air Preheater to Boiler Condensate Return Tank Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN60CT001XQ01 | B2LCN60CT001 | XQ01 | B2: LP Cond Seal AirPreHtr to Blr Cnd Rtn Tnk Temp | B2: LP Condensate Seal Air Preheater to Boiler Condensate Return Tank Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN70AA301XB01 | B2LCN70AA301 | XB01 | B1: HP Pri AirPreHtr Lvl MOV | B1: HP Primary Air Preheater Level Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN70AA301XB02 | B2LCN70AA301 | XB02 | B1: HP Pri AirPreHtr Lvl MOV | B1: HP Primary Air Preheater Level Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN70AA301XB07 | B2LCN70AA301 | XB07 | B1: HP Pri AirPreHtr Lvl MOV | B1: HP Primary Air Preheater Level Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN70AA301XB23 | B2LCN70AA301 | XB23 | B1: HP Pri AirPreHtr Lvl MOV | B1: HP Primary Air Preheater Level Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN70AA301XQ13 | B2LCN70AA301 | XQ13 | B1: HP Pri AirPreHtr Lvl MOV | B1: HP Primary Air Preheater Level Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN70AA301YB01 | B2LCN70AA301 | YB01 | B1: HP Pri AirPreHtr Lvl MOV | B1: HP Primary Air Preheater Level Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN70AA301YB02 | B2LCN70AA301 | YB02 | B1: HP Pri AirPreHtr Lvl MOV | B1: HP Primary Air Preheater Level Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH001 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN70AA401XQ13 | B2LCN70AA401 | XQ13 | B2: HP Pri AirPreHtr Lvl CV | B2: HP Primary Air Preheater Level Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN70AA401YQ01 | B2LCN70AA401 | YQ01 | B2: HP Pri AirPreHtr Lvl CV | B2: HP Primary Air Preheater Level Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN70CF001AXQ01 | B2LCN70CF001A | XQ01 | B2: HP Pri AirPreHtr to Blr Cnd Rtn Tnk Flow 1 | B2: HP Primary Air Preheater to Boiler Condensate Return Tank Flow 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN70CF001BXQ01 | B2LCN70CF001B | XQ01 | B2: HP Pri AirPreHtr to Blr Cnd Rtn Tnk Flow 2 | B2: HP Primary Air Preheater to Boiler Condensate Return Tank Flow 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | FT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN70CP001XQ01 | B2LCN70CP001 | XQ01 | B2: HP Pri AirPreHtr to Blr Cnd Rtn Tnk Press 1 | B2: HP Primary Air Preheater to Boiler Condensate Return Tank Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN70CP002XQ01 | B2LCN70CP002 | XQ01 | B2: HP Pri AirPreHtr to Blr Cnd Rtn Tnk Press 2 | B2: HP Primary Air Preheater to Boiler Condensate Return Tank Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN80AA401XQ13 | B2LCN80AA401 | XQ13 | B2: Stm FluGas HX Cnd Accu Lvl CV | B2: Steam Flue Gas Heat Exchanger Condensate Accumulator Level Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN80AA401YQ01 | B2LCN80AA401 | YQ01 | B2: Stm FluGas HX Cnd Accu Lvl CV | B2: Steam Flue Gas Heat Exchanger Condensate Accumulator Level Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN80CL001AXQ01 | B2LCN80CL001A | XQ01 | B2: Stm FluGas HX Cnd Accu Lvl 1 | B2: Steam Flue Gas Heat Exchanger Condensate Accumulator Level 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN80CL001BXQ01 | B2LCN80CL001B | XQ01 | B2: Stm FluGas HX Cnd Accu Lvl 2 | B2: Steam Flue Gas Heat Exchanger Condensate Accumulator Level 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | LT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN80CP001AXQ01 | B2LCN80CP001A | XQ01 | B2: Stm FluGas HX Cnd Accu Press 1 | B2: Steam Flue Gas Heat Exchanger Condensate Accumulator Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN80CP001BXQ01 | B2LCN80CP001B | XQ01 | B2: Stm FluGas HX Cnd Accu Press 2 | B2: Steam Flue Gas Heat Exchanger Condensate Accumulator Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN80CP010XQ01 | B2LCN80CP010 | XQ01 | B2: Stm FluGas HX to Cnd Accu Press | B2: Steam Flue Gas Heat Exchanger to Condensate Accumulator Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN80CP020XQ01 | B2LCN80CP020 | XQ01 | B2: Cnd FluGas HX Outl Press | B2: Condensate Flue Gas Heat Exchanger Outlet Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN80CP030XQ01 | B2LCN80CP030 | XQ01 | B2: Cnd FluGas HX to Blr Cnd Rtn Tnk Press | B2: Condensate Flue Gas Heat Exchanger to Boiler Condensate Return Tank Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN80CT001XQ01 | B2LCN80CT001 | XQ01 | B2: Cnd FluGas HX Cnd Accu Outl Temp 1 | B2: Condensate Flue Gas Heat Exchanger Condensate Accumulator Outlet Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN80CT002XQ01 | B2LCN80CT002 | XQ01 | B2: Cnd FluGas HX Cnd Accu Outl Temp 2 | B2: Condensate Flue Gas Heat Exchanger Condensate Accumulator Outlet Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN80CT010XQ01 | B2LCN80CT010 | XQ01 | B2: Stm FluGas HX to Cnd Accu Temp | B2: Steam Flue Gas Heat Exchanger to Condensate Accumulator Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN80CT020XQ01 | B2LCN80CT020 | XQ01 | B2: Cnd FluGas HX Outl Temp | B2: Condensate Flue Gas Heat Exchanger Outlet Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN80CT030XQ01 | B2LCN80CT030 | XQ01 | B2: Cnd FluGas HX to Blr Cnd Rtn Tnk Temp | B2: Condensate Flue Gas Heat Exchanger to Boiler Condensate Return Tank Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN81AA401XQ13 | B2LCN81AA401 | XQ13 | B2: Stm FluGas HX Cnd Accu Press CV | B2: Steam Flue Gas Heat Exchanger Condensate Accumulator Pressure Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN81AA401YQ01 | B2LCN81AA401 | YQ01 | B2: Stm FluGas HX Cnd Accu Press CV | B2: Steam Flue Gas Heat Exchanger Condensate Accumulator Pressure Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN81CP001XQ01 | B2LCN81CP001 | XQ01 | B2: Stm FluGas HX Cnd Accu to Cnd Rtn Tnk Press | B2: Steam Flue Gas Heat Exchanger Condensate Accumulator to Condensate Return Tank Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCN81CT001XQ01 | B2LCN81CT001 | XQ01 | B2: Stm FluGas HX Cnd Accu to Cnd Rtn Tnk Temp | B2: Steam Flue Gas Heat Exchanger Condensate Accumulator to Condensate Return Tank Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000010 - Feedwater | NPE7-EAI-41XX-XXX-PP-XA-007606 | NPE7-EAI-41XX-XXX-PP-XA-007625 | NPE7-EAI-41XX-XXX-IM-XA-007654 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCQ10CP001XQ01 | B2LCQ10CP001 | XQ01 | B2: BlwDn Pmps Suct Press | B2: Blowdown Pumps Suction Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCQ10CT001AXQ01 | B2LCQ10CT001A | XQ01 | B2: BlwDn Pmps Suct Temp 1 | B2: Blowdown Pumps Suction Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCQ10CT001BXQ01 | B2LCQ10CT001B | XQ01 | B2: BlwDn Pmps Suct Temp 2 | B2: Blowdown Pumps Suction Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCQ11CP001XQ01 | B2LCQ11CP001 | XQ01 | B2: BlwDn Pmp1 Suct Filtr DP | B2: Blowdown Pump 1 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCQ12CP001XQ01 | B2LCQ12CP001 | XQ01 | B2: BlwDn Pmp2 Suct Filtr DP | B2: Blowdown Pump 2 Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCQ13CP001XQ01 | B2LCQ13CP001 | XQ01 | B2: Emerg BlwDn Pmp Suct Press | B2: Emergency Blowdown Pump Suction Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCQ13CP002XQ01 | B2LCQ13CP002 | XQ01 | B2: Emerg BlwDn Pmp Suct Filtr DP | B2: Emergency Blowdown Pump Suction Filter Differential Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCQ13CT001AXQ01 | B2LCQ13CT001A | XQ01 | B2: Emerg BlwDn Pmp Suct Temp 1 | B2: Emergency Blowdown Pump Suction Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCQ13CT001BXQ01 | B2LCQ13CT001B | XQ01 | B2: Emerg BlwDn Pmp Suct Temp 2 | B2: Emergency Blowdown Pump Suction Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCQ15AA401XQ13 | B2LCQ15AA401 | XQ13 | B2: Emerg BlwDn Pmp Disch CV | B2: Emergency Blowdown Pump Discharge Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCQ15AA401YQ01 | B2LCQ15AA401 | YQ01 | B2: Emerg BlwDn Pmp Disch CV | B2: Emergency Blowdown Pump Discharge Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCQ15CP001XQ01 | B2LCQ15CP001 | XQ01 | B2: Emerg BlwDn Pmp Disch Press | B2: Emergency Blowdown Pump Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCQ25AA401XQ13 | B2LCQ25AA401 | XQ13 | B2: BlwDn Pmps Disch CV | B2: Blowdown Pumps Discharge Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCQ25AA401YQ01 | B2LCQ25AA401 | YQ01 | B2: BlwDn Pmps Disch CV | B2: Blowdown Pumps Discharge Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2LCQ25CP001XQ01 | B2LCQ25CP001 | XQ01 | B2: BlwDn Pmps Disch Press | B2: Blowdown Pumps Discharge Pressure | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH001 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41AC-XXX-PD-XA-000005 - Boiler Blowdown System | NPE7-EAI-41AC-XXX-PP-XA-007639 | NPE7-EAI-41AC-XXX-PP-XA-007740 | NPE7-EAI-41AC-XXX-IM-XA-007646 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2MAN10AA301XB01 | B2MAN10AA301 | XB01 | B2: MS Pot Inl Bypass CV Drn MOV | B2: Main Steam Pot Inlet Bypass Control Valve Drain Motor Operated Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2MAN10AA301XB02 | B2MAN10AA301 | XB02 | B2: MS Pot Inl Bypass CV Drn MOV | B2: Main Steam Pot Inlet Bypass Control Valve Drain Motor Operated Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2MAN10AA301XB07 | B2MAN10AA301 | XB07 | B2: MS Pot Inl Bypass CV Drn MOV | B2: Main Steam Pot Inlet Bypass Control Valve Drain Motor Operated Valve | Actuator Fault |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2MAN10AA301XB23 | B2MAN10AA301 | XB23 | B2: MS Pot Inl Bypass CV Drn MOV | B2: Main Steam Pot Inlet Bypass Control Valve Drain Motor Operated Valve | Actuator Local Mode |  |  |  | DI | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2MAN10AA301XQ13 | B2MAN10AA301 | XQ13 | B2: MS Pot Inl Bypass CV Drn MOV | B2: Main Steam Pot Inlet Bypass Control Valve Drain Motor Operated Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2MAN10AA301YB01 | B2MAN10AA301 | YB01 | B2: MS Pot Inl Bypass CV Drn MOV | B2: Main Steam Pot Inlet Bypass Control Valve Drain Motor Operated Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2MAN10AA301YB02 | B2MAN10AA301 | YB02 | B2: MS Pot Inl Bypass CV Drn MOV | B2: Main Steam Pot Inlet Bypass Control Valve Drain Motor Operated Valve | Cl Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM01GH004 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2MAN10AA401XQ13 | B2MAN10AA401 | XQ13 | B2: Main Steam Bypass CV | B2: Main Steam Bypass Control Valve | Position Ind | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2MAN10AA401YQ01 | B2MAN10AA401 | YQ01 | B2: Main Steam Bypass CV | B2: Main Steam Bypass Control Valve | Position Demand | N/A |  |  | AO | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2MAN10CP001AXQ01 | B2MAN10CP001A | XQ01 | B2: MS Bypass to ACC Press 1 | B2: Main Steam Bypass to Air Cooled Condenser Pressure 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2MAN10CP001BXQ01 | B2MAN10CP001B | XQ01 | B2: MS Bypass to ACC Press 2 | B2: Main Steam Bypass to Air Cooled Condenser Pressure 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | PT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2MAN10CT001AXQ01 | B2MAN10CT001A | XQ01 | B2: MS Bypass to ACC Temp 1 | B2: Main Steam Bypass to Air Cooled Condenser Temperature 1 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | A | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2MAN10CT001BXQ01 | B2MAN10CT001B | XQ01 | B2: MS Bypass to ACC Temp 2 | B2: Main Steam Bypass to Air Cooled Condenser Temperature 2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 | B | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2MAN10CT001XQ01 | B2MAN10CT001 | XQ01 | B2: MS Pot Inl Bypass Temp | B2: Main Steam Pot Inlet Bypass Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH004 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000002 - Main Steam, Extractions Auxiliary Steam & By-Pass | NPE7-EAI-41XX-XXX-PP-XA-007604 | NPE7-EAI-41XX-XXX-PP-XA-007624 | NPE7-EAI-41XX-XXX-IM-XA-007653 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2PGB21CT001XQ01 | B2PGB21CT001 | XQ01 | B2: FdHoprCoolSyst to FFC Temp | B2: Feed Hopper Cooling System SteamTurbine to Fin Fan Coolers Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2PGB22CT001XQ01 | B2PGB22CT001 | XQ01 | B2: Comb Cam1 to FFC Temp | B2: Combustion Camera 1 to Fin Fan Coolers Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2PGB23CT001XQ01 | B2PGB23CT001 | XQ01 | B2: Comb Cam2 to FFC Temp | B2: Combustion Camera 2 to Fin Fan Coolers Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | B2PGB24CT001XQ01 | B2PGB24CT001 | XQ01 | B2: HydrcStn to FFC Temp | B2: Hydraulic Station to Fin Fan Coolers Temperature | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM02GH002 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000007 - Closed Cooling Water | NPE7-EAI-41XX-XXX-PP-XA-007611 | NPE7-EAI-41XX-XXX-PP-XA-007630 | NPE7-EAI-41XX-XXX-IM-XA-007612 |  | Hold | TT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B2QUB10CQ001XQ01 | B2QUB10CQ001 | XQ01 | B2: Live Steam DC | B2: Isolation Valve Steam DC | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B2QUB10CQ002XQ01 | B2QUB10CQ002 | XQ01 | B2: Live Steam AC | B2: Isolation Valve Steam AC | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B2QUB10CQ003XQ01 | B2QUB10CQ003 | XQ01 | B2: Live Steam SIO2 | B2: Isolation Valve Steam SIO2 | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B2QUB10CQ004XQ01 | B2QUB10CQ004 | XQ01 | B2: Live Steam DCC | B2: Isolation Valve Steam DCC | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B2QUH30CQ001XQ01 | B2QUH30CQ001 | XQ01 | B2: Boiler Water DC | B2: Boiler Water DC | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B2QUH30CQ002XQ01 | B2QUH30CQ002 | XQ01 | B2: Boiler Water AC | B2: Boiler Water AC | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Sampling Supplier | B2QUH30CQ003XQ01 | B2QUH30CQ003 | XQ01 | B2: Boiler Water PH | B2: Boiler Water PH | N/A | N/A |  |  | AI | 4-20mA | S |  |  | B0CRM01GH003 |  | TBD | TBD | TBD | TBD | TBD | TBD |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000014 - Sampling | NPE7-EAI-41XX-XXX-PP-XA-007616 | NPE7-EAI-41XX-XXX-PP-XA-007635 | NPE7-EAI-41XX-XXX-IM-XA-007616 |  | Hold | QT |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Cadent | F0EKG01AA301XB01 | F0EKG01AA301 | XB01 | Natural Gas Inlet ESD Valve | Natural Gas Inlet ESD Valve | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000011 - Natural Gas | NPE7-EAI-41XX-XXX-PP-XA-007643 | NPE7-EAI-41XX-XXX-PP-XA-007646 | NPE7-EAI-41XX-XXX-IM-XA-007643 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Cadent | F0EKG01AA301XB02 | F0EKG01AA301 | XB02 | Natural Gas Inlet ESD Valve | Natural Gas Inlet ESD Valve | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000011 - Natural Gas | NPE7-EAI-41XX-XXX-PP-XA-007643 | NPE7-EAI-41XX-XXX-PP-XA-007646 | NPE7-EAI-41XX-XXX-IM-XA-007643 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Cadent | F0EKG01AA301XB19 | F0EKG01AA301 | XB19 | Natural Gas Inlet ESD Valve | Natural Gas Inlet ESD Valve | Emerg Close pushbutton |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000011 - Natural Gas | NPE7-EAI-41XX-XXX-PP-XA-007643 | NPE7-EAI-41XX-XXX-PP-XA-007646 | NPE7-EAI-41XX-XXX-IM-XA-007643 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Cadent | F0EKG01AA301XB20 | F0EKG01AA301 | XB20 | Natural Gas Inlet ESD Valve | Natural Gas Inlet ESD Valve | Emerg Close reset |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000011 - Natural Gas | NPE7-EAI-41XX-XXX-PP-XA-007643 | NPE7-EAI-41XX-XXX-PP-XA-007646 | NPE7-EAI-41XX-XXX-IM-XA-007643 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
Cadent | F0EKG01AA301YB01 | F0EKG01AA301 | YB01 | Natural Gas Inlet ESD Valve | Natural Gas Inlet ESD Valve | Op Cmd |  |  |  | DO | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000011 - Natural Gas | NPE7-EAI-41XX-XXX-PP-XA-007643 | NPE7-EAI-41XX-XXX-PP-XA-007646 | NPE7-EAI-41XX-XXX-IM-XA-007643 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
GRMS Supplier | F0EKG20EA001XB31 | F0EKG20EA001 | XB31 | GRMS SKID | GRMS SKID | n Cmmn Alarm |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000011 - Natural Gas | NPE7-EAI-41XX-XXX-PP-XA-007643 | NPE7-EAI-41XX-XXX-PP-XA-007646 | NPE7-EAI-41XX-XXX-IM-XA-007643 | Gas Regulation and Metering Station | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
GRMS Supplier | F0EKG20EA001XB33 | F0EKG20EA001 | XB33 | GRMS SKID PLC | GRMS SKID PLC | PLC n fail |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000011 - Natural Gas | NPE7-EAI-41XX-XXX-PP-XA-007643 | NPE7-EAI-41XX-XXX-PP-XA-007646 | NPE7-EAI-41XX-XXX-IM-XA-007643 | Gas Regulation and Metering Station | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | F0EKG40AA001XB01 | F0EKG40AA001 | XB01 | Natural Gas Outl Valve Open | Natural Gas Outlet Valve Open | Open |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000011 - Natural Gas | NPE7-EAI-41XX-XXX-PP-XA-007643 | NPE7-EAI-41XX-XXX-PP-XA-007646 | NPE7-EAI-41XX-XXX-IM-XA-007643 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24
EA-I&C | F0EKG40AA001XB02 | F0EKG40AA001 | XB02 | Natural Gas Outl Valve Close | Natural Gas Outlet Valve Close | Closed |  |  |  | DI | 24VDC | S |  |  | B0CRM02GH002 |  | N/A | N/A | N/A | N/A | N/A | N/A |  |  | YES | NPE7-EAI-41XX-XXX-PD-XA-000011 - Natural Gas | NPE7-EAI-41XX-XXX-PP-XA-007643 | NPE7-EAI-41XX-XXX-PP-XA-007646 | NPE7-EAI-41XX-XXX-IM-XA-007643 |  | N/A | - |  | TBD | TBD | [18 empty] | Estimate | TBD |  | A | P01 |  | 2023-03-24

## HW IO Database Fields Desc.
Index | Column Name | Data Type | Field Size | Description | Responsibility
(Note 1)
1 | OWNER | Text | 10 | Responsible party for IO point. Examples are: EA-E, EA-I&C, SIEMENS, WOOD, etc. | PE
2 | POINTNAME | Text | 17 | Signal ID (Key field) | PE
3 | FLD_DEV | Text | 12 | Device tag name (1st and 2nd KKS level identification) | PE
4 | 3_KKS | Text | 5 | 3rd KKS level | PE
5 | DESC (Note 2) | Text | 30 | Abbreviated device description, following Abbreviation List doc. NPE7-EAI-41XX-XXX-RG-XA-007520 | PE
6 | LONG DESC | Text | 150 | Description of the signal | PE
7 | ACTIVE (Note 2) | Text | 10 | For booleans, logic “1” description | PE
8 | INACTIVE (Note 2) | Text | 10 | For booleans, logic “0” description | PE
9 | EST | Text | 1 | For booleans, enter "1" for give an alarm in the CMS for the ACTIVE status or "0" for the INACTIVE status. If left blank no alarm is required in the CMS | PE
10 | PRI | Text | 1 | Priority level alarm in CMS | PE
11 | SIG_TYPE | Text | 2 | Select from the following types: | PE
DI: Digital input
DO: Digital output
AI: Analog input
AO: Analog output
12 | SIG_LEVEL | Text | 10 | Input voltage level for SIG_TYPE: 4-20 mA, 24 VDC, NAMUR, TCE (Thermocouple type E), TCK (Thermocouple type K), RTD, etc. | PE
13 | PWR_SRC | Text | 1 | Signal power source: | PE
F: for field wetted signals
S: (system) for CMS powered signals
14 | NOMINAL POWER | Text | 30 | Nominal power of the device. Determins if the device can be powered from IO module. | PE
15 | LINE MONITORING | Yes/No | - | If empty no line monitoring required | PE
16 | LOCATION | Text | 25 | Physical location where the CMS Cabinet and associated termination board is located. A location may have multiple cabinets from different controllers | PE
17 | DEV_PARTITION | Text | 1 | This field is used to determine which termination boards to assign an I/O point during panel layout. For example, if 3 analog inputs have an A, B and C partition, three separate I/O cards will be assigned during engineering to these points, one for each inputs. This column also applies to redundant pumps, valves, etc. | PE
18 | DEVICE_LO | Number | - | For analog, 0% of the device calibration range (4 mA) | PE
19 | DEVICE_HI | Number | - | For analog, 100% of the device calibration range (20 mA) | PE
20 | DEVICE_UNITS | Text | 8 | For analog, engineering units of the device calibration range | PE
21 | DISPLAY_LO | Number | - | For analog, 0% of display value | PE
22 | DISPLAY_HI | Number | - | For analog, 100% of display value | PE
23 | DISPLAY_UNITS | Text | 8 | For analog, engineering units of display value | PE
24 | PRECISION | Number | - | Analog scaling precision - defines the number of decimal places. If blank will be calculated based on display low and high values. | PE
25 | SOE | Yes/No | - | Use checkbox, if point is used for sequence of events. | PE
26 | HIST | Yes/No | - | Use checkbox, if point signal is to be stored in the Historian. | PE
27 | PID | Text | 30 | P&ID KKS where device/equipment is depicted | PE
28 | LOGIC | Text | 30 | Control logic diagram KKS where device is depicted | PE
29 | SCHEM | Text | 30 | Wiring diagram KKS where device is depicted | PE
30 | HMI_SCREEN | Text | 10 | HMI Screen ID where the device is depicted | PE
31 | Intelligent System | Text | 50 | Name of the system the signal belongs to, in accordance to "Intelligent systems list" doc nº NPE7-HZI-41AC-XXX-RG-XA-00001, if applicable. | PE
32 | Signal Loss | Text | 20 | CMS action in case the signal is lost. Set the value to minimum, maximum or hold the last valid value (Min, Max, Hold) | PE
33 | Instrument Function | Text | 10 | Functional identification of the signal according to DIN19227 (ISA-S5.1). | PE
34 | KKS_Junction Box | Text | 12 | KKS number of the junction box the signal is wired to, if applicable. | PE
35 | Explosion Protection | Text | 30 | Explosion protection marking in accordance with IEC60079 or ATEX, if signal is coming from a hazardous area. For example: Ex ia IIC T6, II 1D T6 | PE
36 | IS | Yes/No | - | Indicate if Intrinsically safety barrier is | PE
required for this signal
37 | IS_MODEL | Texto | 16 | Intrinsically safety barrier Model nº | CMS
38 | IS_IN_TB_1 | Text | 10 | Intrinsically safety barrier input terminal block | CMS
(+)
39 | IS_IN_TB_2 | Text | 10 | Intrinsically safety barrier input terminal block | CMS
(-)
40 | IS_OUT_TB_1 | Text | 10 | Intrinsically safety barrier output terminal | CMS
block (+)
41 | IS_OUT_TB_1 | Text | 10 | Intrinsically safety barrier output terminal | CMS
block (-)
42 | CONTROLLER | Text | 8 | CMS controller ID where signal will be processed | CMS
43 | CABINET_KKS | Text | 20 | CMS cabinet ID where the card associated to the signals is located | CMS
44 | CARD_ID | Text | 16 | CMS card ID within the cabinet | CMS
45 | CARD_TYPE | Text | 15 | Card model | CMS
46 | CARD_POINT_Nº | Number | - | I/O card point where signal will be assigned | CMS
47 | TA_MODEL | Text | 16 | Terminal Assembly Model | CMS
48 | TA_TAG_ID | Text | 16 | Terminal Assembly tag identification | CMS
49 | MC_ID | Text | 16 | Marshalling cabinet ID where the signal from field is hardwired | CMS
50 | MC_TERM_STRIP_ID | Text | 16 | Marshalling terminal strip ID where the signal from field is hardwired | CMS
51 | TB_1 | Text | 10 | Marshalling terminal block 1st (+) | CMS
52 | TB_2 | Text | 10 | Marshalling terminal block 2nd (-) | CMS
53 | TB_3 | Text | 10 | Marshalling terminal block 3rd | CMS
54 | TB_4 | Text | 10 | Marshalling terminal block 4th | CMS
55 | STATUS OF TECHNICAL DATA | Estimation/Final | - | Information related to reliability of the specified technical data, is the data based on estimation or supplier's datasheed | PE
56 | IN PAMELA | Yes/No | - | If the signal is transferred to performance monitoring system Pamela | PE
57 | REMARKS | Text | 255 | Field for general remarks | PE
58 | MOD | Text | 2 | Modification code indicating a change occurred: | PE
A: Added
M: Modified
D: Deleted
59 | REV | Text | 2 | Revision - indicates the revision for the change. If the modification code has been changed this field should be also updated | PE
60 | REV_COMMENT | Text | 255 | Revision comment. Explains the changes in the signal | PE
61 | REV_DATE | Date/Time | - | Date when signal was entered or revised | PE
Note 1: CMS (CMS Supplier), PE (Process Engineer).
Note 2: For Booleans the description of the signal is obtained by concatenating the fields “DESC” and “ACTIVE”. For analog signals, the signal description will be the field "DESC”.

## Notes
I/O Data Base
| Project: | NORTH LONDON
CMS signals notes: 1- Preliminary signals: - Feedwater pumps instrumentation. - Condensate pumps instrumentation. - Potable Water pressure unit signals. - Service Water pressure unit signals. - Drinking Water pressure unit signals. - Rain Water pressure unit signals. - GRMS signals. - Natural Gas Inlet ESD Valve signals. - CEMS signals. - WEMS signals. - Chemical Dosing System signals. - Sampling System signals. - Water Treatment Plant Interface signals. - Firefighting System signals. - Clinical Waste Treatment System signals. - Raw Water Motorized Travelling EEL Screen Filter signals.
2- Pending signals: - Electrical Systems signals. - Air Cooled Condenser signals. - Fin Fan Cooler signals. - Steam Turbine Interface signals. - Closed Cooling Water pumps instrumentation. - Vacuum Ejectors Condenser Signals. - TRAFFIC MANAGEMENT SYSTEM: Weighbridge signals - Air Traffic Warning signals. - Waste crane signals. - IBA crane signals. - Clinical Waste signals. - Odour Control System signals - Vacuum System signals - Electric Heat Tracing signals.